## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 1001
EPA ID No. | TXD084970169
Facility Name | Lonza, Inc.
Facility Location
City | Pasadena
State | TX
Unit ID Name/No. | Boiler B-4001C
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid injection
Combustor Characteristics | 38.5 MM Btu/hr capacity with 32,000 lb/hr steam @ 125 psig
Capacity (MMBtu/hr) | 39
Soot Blowing | Yes
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics
Hazardous Wastes | Liq
Haz Waste Description | Liquid organic wastes
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 2.9583
Height (ft) | 52
Gas Velocity (ft/sec) | 16.9
Gas Temperature (°F) | 426
Permitting Status
HWC Burn Status (Date if Terminated)

## cond
Cond Description
1001C1
Report Name/Date | Certification of Compliance for Boilers A/B & C; 5/23/97
Report Preparer | IT Corp
Testing Firm | IT Corp
Testing Dates | 1997-02-19
Cond Dates | 1997-02-01
Cond Description | CoC; max waste (T-4014) feedrate
Content | PM, CO emissions; ash, chlorides, metals in feeds
1001C2
Report Name/Date | Certification of Compliance for Boilers A/B & C; 5/23/97
Report Preparer | IT Corp
Testing Firm | IT Corp
Testing Dates | 1997-02-21
Cond Dates | 1997-02-01
Cond Description | CoC; max waste (G-3102) feedrate
Content | PM, CO emissions; ash, chlorides, metals in feeds
1001C3
Report Name/Date | Certification of Compliance for Boilers A/B & C; 5/23/97
Report Preparer | IT Corp
Testing Firm | IT Corp
Testing Dates | 1997-02-24
Cond Dates | 1997-02-01
Cond Description | CoC; max waste (T-4053) feedrate
Content | PM, CO emissions; ash/chlorides/metals in feeds
1001C4
Report Name/Date | Certification of Compliance for Boilers A/B & C; 5/23/97
Report Preparer | IT Corp
Testing Firm | IT Corp
Testing Dates | 1997-04-20
Cond Dates | 1997-04-01
Cond Description | CoC; minimum combustion temperature
Content | CO emissions

## emiss
Stack Gas Emissions
| Cond ID | Comments | Units | 7% O2
1 | 1001C1 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0026 | 0.0031 | 0.0038 | 0.0029
| CO (MHRA) | E1 | ppmv | y | 8.7 | 9 | 33.9 | 17.2
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 7306 | 6146 | 4119 | 5857
| O2 |  | % |  | 5.2 | 5 | 5.2 | 5.1333
| Moisture |  | % |  | 15.1 | 15.2 | 14.9 | 15.0667
| Temperature |  | °F |  | 437.5 | 453.8 | 398.8 | 430.0333
Sootblow
2 | 1001C2 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0032 | 0.0023 | 0.0018 | 0.0027
| CO (MHRA) | E1 | ppmv | y | 31 | 38.6 | 41.2 | 36.9
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 6616 | 6517 | 5530 | 6221
| O2 |  | % |  | 5.16 | 4.96 | 5.03 | 5.05
| Moisture |  | % |  | 13.3 | 13.3 | 19.6 | 15.4
| Temperature |  | °F |  | 426.1 | 425.5 | 426.8 | 426.1333
Sootblow
3 | 1001C3 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0029 | 0.0019 | 0.0013 | 0.0024
| CO (MHRA) | E1 | ppmv | y | 33.2 | 23.8 | 26.1 | 27.7
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 7147 | 7477 | 7672 | 7432
| O2 |  | % |  | 5.18 | 4.97 | 5.03 | 5.06
| Moisture |  | % |  | 12.3 | 12.3 | 12.3 | 12.3
| Temperature |  | °F |  | 448 | 449 | 449 | 448.6667
4 | 1001C4 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (MHRA) | E1 | ppmv | y | 10 | 0.9 | 1 | 4

## feed
Feedstreams
* | 1001C1 |  |  | Cond Avg | Cond Avg | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 | F2 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW | Spike | Natural Gas |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW | Spike | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Liq waste | Spike | Nat gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate | g/hr |  | 388300
| Feed Rate | scfh |  |  |  | 19800
| Viscosity | cSt |  | 5.17
| Heating Value | Btu/lb |  | 8400
| Ash | g/hr |  | 119 | 160 |  |  | 289 |  | 220 |  | 328
| Chlorine | g/hr |  | 100 |  |  |  | 114.2 |  | 97.6 |  | 92.4
| Mercury | g/hr | nd | 0.019 |  |  | nd | 0.018 | nd | 0.019 | nd | 0.021
| Lead | g/hr | nd | 0.39 |  |  | nd | 0.37 | nd | 0.37 | nd | 0.43
| Cadmium | g/hr | nd | 0.019 |  |  | nd | 0.018 | nd | 0.019 | nd | 0.021
| Arsenic | g/hr | nd | 0.019 |  |  | nd | 0.018 | nd | 0.019 | nd | 0.021
| Beryllium | g/hr | nd | 0.019 |  |  | nd | 0.018 | nd | 0.019 | nd | 0.021
| Chromium | g/hr | nd | 0.019 |  |  | nd | 0.018 | nd | 0.019 | nd | 0.021
| Antimony | g/hr | nd | 0.39 |  |  | nd | 0.37 | nd | 0.37 | nd | 0.43
| Stack Gas Flowrate | dscfm |  | 5857 | 5857 | 5857 |  | 7306 |  | 6146 |  | 4119
| O2 | % |  | 5.1333 | 5.1333 | 5.1333 |  | 5.2 |  | 5 |  | 5.2
| Thermal Feedrate | MMBtu/hr |  | 7.1907 |  | 19.8 | [7 empty] | 26.9907
| Estimated Firing Rate | MMBtu/hr | [11 empty] | 29.5019
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 10.5502 | 14.1851 |  |  | 20.642 |  | 18.4459 |  | 41.5542 |  | 26.8807
| Chlorine | µg/dscm |  | 8865.7112 |  |  |  | 8156.7978 |  | 8183.2841 |  | 11706.1327 |  | 9348.7382
| Mercury | µg/dscm | 100 | 1.6845 |  |  | 100 | 1.2857 | 100 | 1.5931 | 100 | 2.6605 | 100 | 0.9232
| Lead | µg/dscm | 100 | 34.5763 |  |  | 100 | 26.4275 | 100 | 31.0227 | 100 | 54.4766 | 100 | 18.6545
| Cadmium | µg/dscm | 100 | 1.6845 |  |  | 100 | 1.2857 | 100 | 1.5931 | 100 | 2.6605 | 100 | 0.9232
| Arsenic | µg/dscm | 100 | 1.6845 |  |  | 100 | 1.2857 | 100 | 1.5931 | 100 | 2.6605 | 100 | 0.9232
| Beryllium | µg/dscm | 100 | 1.6845 |  |  | 100 | 1.2857 | 100 | 1.5931 | 100 | 2.6605 | 100 | 0.9232
| Chromium | µg/dscm | 100 | 1.6845 |  |  | 100 | 1.2857 | 100 | 1.5931 | 100 | 2.6605 | 100 | 0.9232
| Antimony | µg/dscm | 100 | 34.5763 |  |  | 100 | 26.4275 | 100 | 31.0227 | 100 | 54.4766 | 100 | 18.6545
| SVM | µg/dscm | 100 | 18.1304 |  |  | 100 | 13.8566 | 100 | 16.3079 | 100 | 28.5685 | 100 | 19.5777
| LVM | µg/dscm | 100 | 2.5267 |  |  | 100 | 1.9285 | 100 | 2.3896 | 100 | 3.9907 | 100 | 2.7696
* | 1001C2 |  |  | Cond Avg | Cond Avg | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 | F2 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW | Spike | Natural Gas |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW | Spike | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Liq waste | Spike | Nat gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate | g/hr |  | 340000
| Feed Rate | scfh |  |  |  | 15400
| Viscosity | cSt |  | 3.04
| Heat Content | Btu/lb |  | 8200
| Ash | g/hr |  | 3 | 164 |  |  | 152 |  | 178 |  | 171
| Chlorine | g/hr |  | 99 |  |  |  | 108.3 |  | 88.6 |  | 100.6
| Mercury | g/hr | nd | 0.017 |  |  | nd | 0.018 | nd | 0.017 | nd | 0.017
| Lead | g/hr | nd | 0.34 |  |  | nd | 0.35 | nd | 0.33 | nd | 0.34
| Cadmium | g/hr | nd | 0.017 |  |  | nd | 0.018 | nd | 0.017 | nd | 0.017
| Arsenic | g/hr | nd | 0.017 |  |  | nd | 0.018 | nd | 0.017 | nd | 0.017
| Beryllium | g/hr | nd | 0.017 |  |  | nd | 0.018 | nd | 0.017 | nd | 0.017
| Chromium | g/hr | nd | 0.017 |  |  | nd | 0.018 | nd | 0.017 | nd | 0.017
| Antimony | g/hr | nd | 0.34 |  |  | nd | 0.35 | nd | 0.33 | nd | 0.34
| Stack Gas Flowrate | dscfm |  | 6221 | 6221 |  |  | 6616 |  | 6517 |  | 5530
| O2 | % |  | 5.05 | 5.05 |  |  | 5.16 |  | 4.96 |  | 5.03
| Thermal Feedrate | MMBtu/hr |  | 6.1464 |  | 15.4 | [7 empty] | 21.5464
| Estimated Firing Rate | MMBtu/hr | [11 empty] | 31.5
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 0.2491 | 13.6175 |  |  | 11.9587 |  | 14.0397 |  | 15.9645 |  | 13.9876
| Chlorine | µg/dscm |  | 8220.3216 |  |  |  | 8520.5599 |  | 6988.3072 |  | 9392.0043 |  | 8300.2905
| Mercury | µg/dscm | 100 | 1.4116 |  |  | 100 | 1.4162 | 100 | 1.3409 | 100 | 1.5871 | 100 | 1.448
| Lead | µg/dscm | 100 | 28.2314 |  |  | 100 | 27.5364 | 100 | 26.0287 | 100 | 31.7424 | 100 | 28.4358
| Cadmium | µg/dscm | 100 | 1.4116 |  |  | 100 | 1.4162 | 100 | 1.3409 | 100 | 1.5871 | 100 | 1.448
| Arsenic | µg/dscm | 100 | 1.4116 |  |  | 100 | 1.4162 | 100 | 1.3409 | 100 | 1.5871 | 100 | 1.448
| Beryllium | µg/dscm | 100 | 1.4116 |  |  | 100 | 1.4162 | 100 | 1.3409 | 100 | 1.5871 | 100 | 1.448
| Chromium | µg/dscm | 100 | 1.4116 |  |  | 100 | 1.4162 | 100 | 1.3409 | 100 | 1.5871 | 100 | 1.448
| Antimony | µg/dscm | 100 | 28.2314 |  |  | 100 | 27.5364 | 100 | 26.0287 | 100 | 31.7424 | 100 | 28.4358
| SVM | µg/dscm | 100 | 14.8215 |  |  | 100 | 14.4763 | 100 | 13.6848 | 100 | 16.6647 | 100 | 14.9419
| LVM | µg/dscm | 100 | 2.1174 |  |  | 100 | 2.1242 | 100 | 2.0113 | 100 | 2.3807 | 100 | 2.1721
* | 1001C3 |  |  | Cond Avg | Cond Avg | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 | F2 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW | Spike | Natural Gas |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW | Spike | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Liq waste | Spike | Nat gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate | g/hr |  | 270000
| Feed Rate | scfh |  |  |  | 15600
| Viscosity | cSt |  | 2.93
| Heat Content | Btu/lb |  | 16800
| Ash | g/hr |  | 3 | 180 |  |  | 186 |  | 179 |  | 183
| Chlorine | g/hr |  | 61 |  |  |  | 66.2 |  | 54.5 |  | 61.8
| Mercury | g/hr | nd | 0.014 |  |  | nd | 0.014 | nd | 0.013 | nd | 0.014
| Lead | g/hr | nd | 0.27 |  |  | nd | 0.28 | nd | 0.26 | nd | 0.27
| Cadmium | g/hr | nd | 0.014 |  |  | nd | 0.014 | nd | 0.013 | nd | 0.014
| Arsenic | g/hr | nd | 0.014 |  |  | nd | 0.014 | nd | 0.013 | nd | 0.014
| Beryllium | g/hr | nd | 0.014 |  |  | nd | 0.014 | nd | 0.013 | nd | 0.014
| Chromium | g/hr | nd | 0.014 |  |  | nd | 0.014 | nd | 0.013 | nd | 0.014
| Antimony | g/hr | nd | 0.27 |  |  | nd | 0.28 | nd | 0.26 | nd | 0.27
| Stack Gas Flowrate | dscfm |  | 7432 | 7432 |  |  | 7147 |  | 7477 |  | 7672
| O2 | % |  | 5.06 | 5.06 |  |  | 5.18 |  | 4.97 |  | 5.03
| Thermal Feedrate | MMBtu/hr |  | 9.9912 |  | 15.6 | [7 empty] | 25.5912
| Estimated Firing Rate | MMBtu/hr | [11 empty] | 37.6083
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 0.20864 | 12.5185 |  |  | 13.5635 |  | 12.3135 |  | 12.3148 |  | 12.7306
| Chlorine | µg/dscm |  | 4242.3874 |  |  |  | 4827.4533 |  | 3749.0907 |  | 4158.7739 |  | 4245.106
| Mercury | µg/dscm | 100 | 0.97366 |  |  | 100 | 1.0209 | 100 | 0.89428 | 100 | 0.94212 | 100 | 0.95244
| Lead | µg/dscm | 100 | 18.7778 |  |  | 100 | 20.4182 | 100 | 17.8856 | 100 | 18.1694 | 100 | 18.8244
| Cadmium | µg/dscm | 100 | 0.97366 |  |  | 100 | 1.0209 | 100 | 0.89428 | 100 | 0.94212 | 100 | 0.95244
| Arsenic | µg/dscm | 100 | 0.97366 |  |  | 100 | 1.0209 | 100 | 0.89428 | 100 | 0.94212 | 100 | 0.95244
| Beryllium | µg/dscm | 100 | 0.97366 |  |  | 100 | 1.0209 | 100 | 0.89428 | 100 | 0.94212 | 100 | 0.95244
| Chromium | µg/dscm | 100 | 0.97366 |  |  | 100 | 1.0209 | 100 | 0.89428 | 100 | 0.94212 | 100 | 0.95244
| Antimony | µg/dscm | 100 | 18.7778 |  |  | 100 | 20.4182 | 100 | 17.8856 | 100 | 18.1694 | 100 | 18.8244
| SVM | µg/dscm | 100 | 9.8757 |  |  | 100 | 10.7196 | 100 | 9.3899 | 100 | 9.5558 | 100 | 9.8884
| LVM | µg/dscm | 100 | 1.4605 |  |  | 100 | 1.5314 | 100 | 1.3414 | 100 | 1.4132 | 100 | 1.4287
BIF Feedrate Limits
| Antimony | g/hr |  | 93.3
| Arsenic | g/hr |  | 0.037
| Barium | g/hr |  | 15333
| Beryllium | g/hr |  | 0.037
| Cadmium | g/hr |  | 0.037
| Chromium | g/hr |  | 0.2
| Lead | g/hr |  | 27.3
| Mercury | g/hr |  | 93.3
| Silver | g/hr |  | 933
| Thallium | g/hr |  | 93.3
| Chlorine | g/hr |  | 123

## process
Process Information
Cond ID No. | Units | Run 1 | Run 2 | Run 3 | Cond Avg
1001C1
Firebox Exit Temp | F | 370 | 377 | 333 | 360
Steam Production Rate | Mlb/hr | 22.6 | 22.4 | 17.5 | 20.8333
1001C2
Firebox Exit Temp | F | 362 | 357 | 357 | 359
Steam Production Rate | Mlb/hr | 17.3 | 16.7 | 16.7 | 16.9
1001C3
Firebox Exit Temp | F | 357 | 357 | 357 | 357
Steam Production Rate | Mlb/hr | 21.5 | 21.4 | 21.1 | 21.3333
1001C4
Firebox Exit Temp | F | 299 | 299 | 299 | 299