## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 1002
EPA ID No. | TXD083472266
Facility Name | Lyondell Chemical Co.
Facility Location
City | Channelview
State | TX
Unit ID Name/No. | Utility Boiler 3
Other Sister Facilities | Utility Boilers 1 and 2
Number of Sister Facilities | 2
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid injection
Combustor Characteristics | Babcock & Wilcox, 600,000 lbs/hr of 750 psig steam, 6 burners
Capacity (MMBtu/hr)
Soot Blowing | Yes (Run # 3 of test condition 1)
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics
Hazardous Wastes | Liq
Haz Waste Description | Liquid waste byproducts (D001, D018, & "LLF")
Supplemental Fuel | Natural gas
Propane purge
Stack Characteristics
Diameter (ft) | 5 x 15 rectangular duct
Height (ft) | 30
Gas Velocity (ft/sec) | 54.65
Gas Temperature (°F) | 311
Permitting Status | Tier I for metals and chloride
HWC Burn Status (Date if Terminated)

## cond
Cond Description
1002C1
Report Name/Date | Recertification of Compliance for F-65630 Hot Oil Heater and Utility Boilers; 8/07/97
Report Preparer | Waste Min Inc.
Testing Firm | Waste Min Inc.
Testing Dates | 1997-07-08
Cond Dates | 1997-07-01
Cond Description | CoC; min combustion temperature
Content | CO emissions only; no feed analysis
1002C2
Report Name/Date | Recertification of Compliance for F-65630 Hot Oil Heater and Utility Boilers; 8/31/98
Report Preparer | Waste Min Inc.
Testing Firm | Waste Min Inc.
Testing Dates | 1998-07-22
Cond Dates | 1998-07-01
Cond Description | CoC; max waste and ash feed
Content | PM, CO emissions only; feed analysis for ash, metals, chlorides
1002C3
Report Name/Date | Recertification of Compliance for F-65630 Hot Oil Heater and Utility Boilers; 8/31/98
Report Preparer | Waste Min Inc.
Testing Firm | Waste Min Inc.
Testing Dates | 1998-07-23
Cond Dates | 1998-07-01
Cond Description | CoC; min combustion temperature
Content | CO emissions only; no feed analysis

## emiss
Stack Gas Emissions
sootblow
| Cond ID | Comments | Units | 7% O2
1 | 1002C1 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) | E1 | ppmv | y | 0 | 0 | 0 | 0
| CO (MHRA) | E1 | ppmv | y | 0 | 0 | 0 | 0
2 | 1002C2 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) | E1 | ppmv | y | 1.42 | 1.45 | 1.32 | 1.3967
| CO (MHRA) | E1 | ppmv | y | 1.46 | 1.53 | 1.44 | 1.4767
| PM | E1 | gr/dscf | y | 0.0088 | 0.007 | 0.0122 | 0.0093
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 138901 | 144713 | 142806 | 142140
| O2 |  | % |  | 6.4 | 5.2 | 4.4 | 5.3333
| Moisture |  | % |  | 15.2 | 15.6 | 16.2 | 15.6667
| Temperature |  | F |  | 310 | 313 | 312 | 311.6667
3 | 1002C3 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (MHRA) | E1 | ppmv | y |  |  |  | 3.5
| CO (RA) | E1 | ppmv | y |  |  |  | 3.23

## feed
Feedstreams
Cond ID No.
* | 1002C1 |  | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  | F1 | F1 | F1 | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 | F4 | F4 | F4 | F4 | F5 | F5 | F5 | F5 | F6 | F6 | F6 | F6 | F7 | F7 | F7 | F7
| Feed Class |  | Liq HW | Liq HW | Liq HW | Liq HW | Liq non-HW | Liq non-HW | Liq non-HW | Liq non-HW | Misc. Fuel | Misc. Fuel | Misc. Fuel | Misc. Fuel | NG | NG | NG | NG | Misc. Fuel | Misc. Fuel | Misc. Fuel | Misc. Fuel | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feedstream Description |  | Pump HW D-6804 | Pump HW D-6804 | Pump HW D-6804 | Pump HW D-6804 | Non hazardous liq | Non hazardous liq | Non hazardous liq | Non hazardous liq | Propane purge | Propane purge | Propane purge | Propane purge | Natural gas | Natural gas | Natural gas | Natural gas | Hydrogen | Hydrogen | Hydrogen | Hydrogen | Ash spike | Ash spike | Ash spike | Ash spike | Total | Total | Total | Total
| Feed Rate | lb/hr | 2000 | 2000 | 2000 | 2000 |  |  |  |  | 420 | 420 | 420 | 420 | 9518 | 9518 | 9518 | 9518
* | 1002C2 |  | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  | F1 | F1 | F1 | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 | F4 | F4 | F4 | F4 | F5 | F5 | F5 | F5 | F6 | F6 | F6 | F6 | F7 | F7 | F7 | F7
| Feed Class |  | Liq HW | Liq HW | Liq HW | Liq HW | Liq non-HW | Liq non-HW | Liq non-HW | Liq non-HW | Misc. Fuel | Misc. Fuel | Misc. Fuel | Misc. Fuel | NG | NG | NG | NG | Misc. Fuel | Misc. Fuel | Misc. Fuel | Misc. Fuel | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Class 2 |  | HW | HW | HW | HW | Non-HW | Non-HW | Non-HW | Non-HW | MF | MF | MF | MF | [9 empty] | Spike | Spike | Spike | Total | Total | Total | Total
| Feedstream Description |  | Pump HW D-6804 | Pump HW D-6804 | Pump HW D-6804 | Pump HW D-6804 | Non hazardous liq | Non hazardous liq | Non hazardous liq | Non hazardous liq | Propane purge | Propane purge | Propane purge | Propane purge | Natural gas | Natural gas | Natural gas | Natural gas | Hydrogen | Hydrogen | Hydrogen | Hydrogen | Ash spike | Ash spike | Ash spike | Ash spike | Total | Total | Total | Total
| Feed Rate | g/hr | 11788148 | 11737558 | 11586624 | 11800000 | 2308059 | 2304881 | 2359087 | 2300000 | 713483 | 691834 | 716508 | 713483 | 5659173 | 5609107 | 5901342 | 5700000 | 1387975 | 1364132 | 1364643 | 1400000 | 88241 | 199089 | 205275 | 88.3
| Heating Value | Btu/lb | 12010.5525 | 11510.1727 | 11710.2652 | 12004.0678 | 18415.2485 | 18716.4023 | 18215.14 | 18475.8261 | 20902.9507 | 20900.823 | 20902.1421 | 20902.9507 | 20619.1046 | 20619.4141 | 20619.2219 | 20469.8246 | 27623.1921 | 27623.4265 | 27623.0633 | 27402.1429
| Thermal Feedrate | MMBtu/hr | 311.855 | 297.58 | 298.86 | 312 | 93.62 | 95.02 | 94.65 | 93.6 | 32.85 | 31.85 | 32.988 | 32.85 | 257.02 | 254.75 | 268.02 | 257 | 84.45 | 83 | 83.03 | 84.5 | 0.097 | 0.22 | 0.226 |  | 779.892 | 762.42 | 777.774 | 779.95
| Ash | g/hr | 2358 | 2348 | 2317 | 2400 | 692 | 2074 | 472 | 700 | [12 empty] | 7430 | 16723 | 10202 | 11451.6667
| Chlorine | g/hr | 330 | 211.28 | 220.15 | 300 | 18.46 | 64.54 | 61.34 | 18 | [12 empty] | 3.88 | 8.36 | 19.71 | 10.65
| Antimony | g/hr | 70.79 | 70.43 | 69.52 | 71 | 13.85 | 13.83 | 14.15 | 14 | [12 empty] | 0.53 | 1.19 | 1.6 | 1.1067
| Arsenic | g/hr | 5.89 | 5.87 | 5.79 | 5.9 | 1.15 | 1.15 | 1.18 | 1.2 | [12 empty] | 0.04 | 0.1 | 0.13 | 0.09
| Barium | g/hr | 5.89 | 5.87 | 5.79 | 5.9 | 1.15 | 1.15 | 1.18 | 1.2 | [12 empty] | 0.04 | 0.1 | 0.13 | 0.09
| Beryllium | g/hr | 5.89 | 5.87 | 5.79 | 5.9 | 1.15 | 1.15 | 1.18 | 1.2 | [12 empty] | 0.04 | 0.1 | 0.13 | 0.09
| Cadmium | g/hr | 5.89 | 5.87 | 5.79 | 5.9 | 1.15 | 1.15 | 1.18 | 1.2 | [12 empty] | 0.04 | 0.1 | 0.13 | 0.09
| Chromium | g/hr | 5.89 | 5.87 | 5.79 | 5.9 | 6.46 | 6.68 | 5.9 | 6 | [12 empty] | 0.04 | 0.1 | 0.13 | 0.09
| Lead | g/hr | 11.79 | 11.74 | 11.59 | 11.8 | 2.31 | 2.3 | 2.36 | 2.3 | [12 empty] | 0.09 | 0.2 | 0.27 | 0.18667
| Mercury | g/hr | 2.95 | 2.93 | 2.9 | 2.95 | 0.58 | 0.58 | 0.59 | 0.6 | [12 empty] | 0.02 | 0.05 | 0.07 | 0.046667
| Silver | g/hr | 11.79 | 11.74 | 11.59 | 11.8 | 2.31 | 2.3 | 2.36 | 2.3 | [12 empty] | 0.09 | 0.2 | 0.27 | 0.18667
| Thallium | g/hr | 5.89 | 5.87 | 5.79 | 5.9 | 1.15 | 1.15 | 1.18 | 1.2 | [12 empty] | 0.04 | 0.1 | 0.13 | 0.09
| Stack Gas Flowrate | dscfm | 138901 | 144713 | 142806 | 142140 | 138901 | 144713 | 142806 | 142140 | 138901 | 144713 | 142806 | 142140 | 138901 | 144713 | 142806 | 142140 | 138901 | 144713 | 142806 | 142140 | 138901 | 144713 | 142806 | 142140
| O2 | % | 6.4 | 5.2 | 4.4 | 5.3333 | 6.4 | 5.2 | 4.4 | 5.3333 | 6.4 | 5.2 | 4.4 | 5.3333 | 6.4 | 5.2 | 4.4 | 5.3333 | 6.4 | 5.2 | 4.4 | 5.3333 | 6.4 | 5.2 | 4.4 | 5.3333
Feedrate MTEC Calculations
| Ash | mg/dscm | 9.5868 | 8.4669 | 8.0586 | 8.7041 | 2.8134 | 7.4788 | 1.6416 | 3.978 | [12 empty] | 30.2079 | 60.3031 | 35.4831 | 41.998 | 42.6082 | 76.2489 | 45.1833 | 54.6801
| Chlorine | µg/dscm | 1341.6711 | 761.8757 | 765.6927 | 956.4131 | 75.0523 | 232.7312 | 213.3436 | 173.709 | [12 empty] | 15.7748 | 30.1462 | 68.5524 | 38.1578 | 1432.4982 | 1024.7531 | 1047.5886 | 1168.2799
| Antimony | µg/dscm | 287.8088 | 253.9706 | 241.794 | 262.8789 | 56.3095 | 49.871 | 49.2144 | 51.8353 | [12 empty] | 2.1548 | 4.2911 | 5.5649 | 4.0975 | 346.2731 | 308.1327 | 296.5733 | 316.993
| Arsenic | µg/dscm | 23.9468 | 21.1672 | 20.1379 | 21.8449 | 4.6755 | 4.1469 | 4.1041 | 4.443 | [12 empty] | 0.16263 | 0.3606 | 0.45215 | 0.33323 | 28.7849 | 25.6747 | 24.6942 | 26.3846
| Barium | µg/dscm | 23.9468 | 21.1672 | 20.1379 | 21.8449 | 4.6755 | 4.1469 | 4.1041 | 4.443 | [12 empty] | 0.16263 | 0.3606 | 0.45215 | 0.33323 | 28.7849 | 25.6747 | 24.6942 | 26.3846
| Beryllium | µg/dscm | 23.9468 | 21.1672 | 20.1379 | 21.8449 | 4.6755 | 4.1469 | 4.1041 | 4.443 | [12 empty] | 0.16263 | 0.3606 | 0.45215 | 0.33323 | 28.7849 | 25.6747 | 24.6942 | 26.3846
| Cadmium | µg/dscm | 23.9468 | 21.1672 | 20.1379 | 21.8449 | 4.6755 | 4.1469 | 4.1041 | 4.443 | [12 empty] | 0.16263 | 0.3606 | 0.45215 | 0.33323 | 28.7849 | 25.6747 | 24.6942 | 26.3846
| Chromium | µg/dscm | 23.9468 | 21.1672 | 20.1379 | 21.8449 | 26.2642 | 24.0881 | 20.5205 | 22.2151 | [12 empty] | 0.16263 | 0.3606 | 0.45215 | 0.33323 | 50.3737 | 45.6159 | 41.1105 | 45.7
| Lead | µg/dscm | 47.9342 | 42.3344 | 40.3106 | 43.6897 | 9.3917 | 8.2938 | 8.2082 | 8.5158 | [12 empty] | 0.36591 | 0.7212 | 0.93907 | 0.69114 | 57.6919 | 51.3494 | 49.4579 | 52.8331
| Mercury | µg/dscm | 11.9937 | 10.5656 | 10.0863 | 10.9224 | 2.3581 | 2.0915 | 2.052 | 2.2215 | [12 empty] | 0.081313 | 0.1803 | 0.24346 | 0.17278 | 14.4331 | 12.8374 | 12.3819 | 13.2174
| Silver | µg/dscm | 47.9342 | 42.3344 | 40.3106 | 43.6897 | 9.3917 | 8.2938 | 8.2082 | 8.5158 | [12 empty] | 0.36591 | 0.7212 | 0.93907 | 0.69114 | 57.6919 | 51.3494 | 49.4579 | 52.8331
| Thallium | µg/dscm | 23.9468 | 21.1672 | 20.1379 | 21.8449 | 4.6755 | 4.1469 | 4.1041 | 4.443 | [12 empty] | 0.16263 | 0.3606 | 0.45215 | 0.33323 | 28.7849 | 25.6747 | 24.6942 | 26.3846
| SVM | µg/dscm | 71.881 | 63.5017 | 60.4485 | 65.5346 | 14.0672 | 12.4407 | 12.3123 | 12.9588 | [12 empty] | 0.52854 | 1.0818 | 1.3912 | 1.0244 | 86.4768 | 77.0242 | 74.152 | 79.2177
| LVM | µg/dscm | 71.8404 | 63.5017 | 60.4137 | 65.5346 | 35.6153 | 32.3819 | 28.7287 | 31.1012 | [12 empty] | 0.48788 | 1.0818 | 1.3564 | 0.99968 | 107.9435 | 96.9653 | 90.4989 | 98.4692
BIF Feedrate Limits
| Antimony | g/hr |  |  |  | 9609
| Arsenic | g/hr |  |  |  | 266
| Barium | g/hr |  |  |  | 1312977
| Beryllium | g/hr |  |  |  | 552
| Cadmium | g/hr |  |  |  | 764
| Chromium | g/hr |  |  |  | 44
| Lead | g/hr |  |  |  | 2288
| Mercury | g/hr |  |  |  | 7625
| Silver | g/hr |  |  |  | 75958
| Thallium | g/hr |  |  |  | 10309
| Chlorine | g/hr |  |  |  | 9609

## process
Process Information
Cond ID No. | Units | Cond Avg
1002C1
Combustion Temperature | °F | 626
1002C2
Combustion Temperature | °F | 1729