## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 1014
EPA ID No. | TXD007376700
Facility Name | Celanese
Facility Location
City | Pampa
State | TX
Unit ID Name/No. | Boiler No. 10
Other Sister Facilities | None (Boiler No. 9 (Phase II ID No. 1013) is identical but was tested separately)
Number of Sister Facilities | 0
Combustor Class | Coal-fired boiler
Combustor Type | Pulverized coal
Combustor Characteristics | Manufactured by Combustion Engineering, Model No. VU-40. Water tube, pulverized coal, corner t-fired, steam generating boiler. 750,000 lbs/hr capacity
Capacity (MMBtu/hr) | 1000
Soot Blowing | No
APCS Detailed Acronym | FF
APCS General Class | FF
APCS Characteristics | Baghouse - 10 compartments w/ teflon finnish filters, effective area 198,720 sq ft.
Hazardous Wastes | Liq
Haz Waste Description | Organic acids and solvent wastes, include but not limited to long-chain carboxylic acids, ketones, esters
Supplemental Fuel | Coal
Pulverized coal, still solids
Stack Characteristics
Diameter (ft)
Height (ft)
Gas Velocity (ft/sec)
Gas Temperature (°F) | 371
Permitting Status | Tier III - Cr; Tier IA - other metals and chlorine
HWC Burn Status (Date if Terminated)

## cond
Cond Description
1014C10
Report Name/Date | Recertification of Compliance (ReCOC) for Celanese Boilers 9 & 10; No date, Report provided begins at Section 2.0
Report Prepare | Focus Environmental
Testing Firm | None Identified
Testing Dates | 1998-09-18
Cond Dates | 1998-09-01
Condition Descr | CoC; max waste feed rate
Content | PM, Cr, CO emissions; feeds for metals, ash, chlorides
1014C11
Report Name/Date | Recertification of Compliance (ReCOC) for Celanese Boilers 9 & 10; No date, Report provided begins at Section 2.0
Report Prepare | Focus Environmental
Testing Firm | None Identified
Testing Dates | 1998-09-16
Cond Dates | 1998-09-01
Condition Descr | CoC; min combustion temp
Content | CO

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
Sootblowing
10 | 1014C10 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0181 | 0.0234 | 0.0138 | 0.018433
| CO (RA) | E1 | ppmv | y | 21.97 | 14.14 | 14.53 | 16.88
| CO (MHRA) | E1 | ppmv | y | 23.9 | 15.6 | 22.7 | 20.7333
| HCl |  | ppmv | n | 1.2501 | 1.2382 | 1.1307 | 1.2063
| Total Chlorine |  | ppmv | n | 0 | 0 | 0 | 0
| Chromium |  | µg/dscm | n | 3.9743 | 4.8456 | 5.0682 | 4.6293
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 199327 | 194365 | 195824 | 196505.3333
| O2 |  | % |  | 6 | 6.2 | 6 | 6.0667
| Moisture |  | % |  | 10.34 | 9.87 | 10.7 | 10.3033
| Temperature |  | °F |  | 367 | 374 | 372 | 371
| Sampling Train | Metals | E2
| Stack Gas Flowrate |  | dscfm |  | 191936 | 187742 | 194002 | 191226.6667
| O2 |  | % |  | 6 | 6.2 | 6 | 6.0667
| Moisture |  | % |  | 10.2 | 10 | 10.2 | 10.1333
| Temperature |  | °F |  | 371 | 378 | 377 | 375.3333
| HCl | E1 | ppmv | y | 1.1667 | 1.1713 | 1.0553 | 1.1311
| Cl2 | E1 | ppmv | y | 0 | 0 | 0 | 0
| Total Chlorine | E1 | ppmv | y | 1.1667 | 1.1713 | 1.0553 | 1.1311
| Chromium | E2 | µg/dscm | y | 3.7093 | 4.5836 | 4.7303 | 4.3411
| LVM | E2 | µg/dscm | y | 3.7 | 4.6 | 4.7 | 4.3
11 | 1014C11 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) | E1 | ppmv | y | 10.26 | 10.1 | 5.92 | 8.76
| CO (MHRA) | E1 | ppmv | y | 16.9 | 13.8 | 7 | 12.5667
| Sampling Train | CO | E1
| Stack Gas Flowrate |  | dscfm
| O2 |  | % |  | 4.2 | 4.14 | 4.18 | 4.1733
| Moisture |  | %
| Temperature |  | °F

## feed
Feedstreams
* | 1014C10 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 | F3 | F3 | F3 | F3 | F4 | F4 | F4 | F4 |  | F5 |  | F5 |  | F5 |  | F5
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Coal |  | Coal |  | Coal |  | Coal | Spike | Spike | Spike | Spike | Misc Fuel | Misc Fuel | Misc Fuel | Misc Fuel |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | Coal |  | Coal |  | Coal |  | Coal | Spike | Spike | Spike | Spike | [5 empty] | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste |  | Waste |  | Waste |  | Waste |  | Coal |  | Coal |  | Coal |  | Coal | Spike | Spike | Spike | Spike | Vent Gas | Vent Gas | Vent Gas | Vent Gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 16850 |  | 17420 |  | 17280 |  | 17183.3333 |  | 58980 |  | 57820 |  | 59060 |  | 58620
| Feed Rate | scfm | [20 empty] | 685.75 | 680.21 | 681.01 | 682.32
| Heating Value | Btu/lb |  | 10149 |  | 10842 |  | 10615 |  | 10535.3333 |  | 12209 |  | 12324 |  | 12290 |  | 12274.3333
| Ash | lb/hr |  | 40.44 |  | 60.97 |  | 50.112 |  | 50.5073 |  | 5715 |  | 5279 |  | 5434 |  | 5476
| Chlorine | lb/hr |  | 0.77 | nd | 0.17 | nd | 0.17 |  | 0.37 | nd | 1.77 | nd | 1.73 | nd | 1.77 |  | 1.7567
| Antimony | lb/hr | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1 | nd | 0.35 | nd | 0.35 | nd | 0.35 |  | 0.35
| Arsenic | lb/hr | nd | 0.02 | nd | 0.02 | nd | 0.02 |  | 0.02 | nd | 0.06 | nd | 0.06 | nd | 0.06 |  | 0.06
| Barium | lb/hr | nd | 0.02 | nd | 0.02 | nd | 0.02 |  | 0.02 |  | 16.57 |  | 16.77 |  | 16.65 |  | 16.6633
| Beryllium | lb/hr | nd | 0 | nd | 0 | nd | 0 |  | 0 |  | 0.02 |  | 0.02 |  | 0.02 |  | 0.02
| Cadmium | lb/hr | nd | 0.01 | nd | 0.01 | nd | 0.01 |  | 0.01 | nd | 0.03 | nd | 0.03 | nd | 0.03 |  | 0.03
| Chromium | lb/hr |  | 0.65 |  | 0.93 |  | 0.86 |  | 0.81333 |  | 0.19 |  | 0.1 |  | 0.09 |  | 0.12667 | 4.1 | 3.92 | 1.98 | 3.3333
| Lead | lb/hr | nd | 0.01 | nd | 0.01 | nd | 0.01 |  | 0.01 | nd | 0.29 | nd | 0.29 | nd | 0.3 |  | 0.29333
| Mercury | lb/hr | nd | 0.00055605 | nd | 0.00057486 | nd | 0.00057024 |  | 0.00056705 | nd | 0.0019463 | nd | 0.0019081 | nd | 0.001949 |  | 0.0019345
| Nickel | lb/hr |  | 0.17 |  | 0.38 |  | 0.22 |  | 0.25667 | nd | 0.24 | nd | 0.23 | nd | 0.24 |  | 0.23667
| Selenium | lb/hr | nd | 0.01 | nd | 0.01 | nd | 0.01 |  | 0.01 |  | 0.1 |  | 0.12 |  | 0.17 |  | 0.13
| Silver | lb/hr | nd | 0.02 | nd | 0.02 | nd | 0.02 |  | 0.02 | nd | 0.06 | nd | 0.06 | nd | 0.06 |  | 0.06
| Thallium | lb/hr | nd | 0.02 | nd | 0.02 | nd | 0.02 |  | 0.02 | nd | 0.06 | nd | 0.06 | nd | 0.06 |  | 0.06
| Zinc | lb/hr | nd | 0.03 | nd | 0.03 | nd | 0.03 |  | 0.03 |  | 0.65 |  | 0.48 |  | 0.45 |  | 0.52667
| Stack Gas Flowrate | dscfm |  | 199327 |  | 194365 |  | 195824 |  | 196505.3333 |  | 199327 |  | 194365 |  | 195824 |  | 196505.3333 | 199327 | 194365 | 195824 | 196505.3333
| Oxygen | % |  | 6 |  | 6.2 |  | 6 |  | 6.0667 |  | 6 |  | 6.2 |  | 6 |  | 6.0667 | 6 | 6.2 | 6 | 6.0667
| Thermal Feedrate | MMBtu/hr |  | 171.0106 |  | 188.8676 |  | 183.4272 |  | 181.1018 |  | 720.0868 |  | 712.5737 |  | 725.8474 |  | 719.5026 | [9 empty] | 891.0975 |  | 901.4413 |  | 909.2746 |  | 900.6045
| Estimated Firing Rate | MMBtu/hr | [31 empty] | 873.357
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 50.6291 |  | 79.3383 |  | 63.8603 |  | 64.6092 |  | 7154.9244 |  | 6869.3886 |  | 6924.8227 |  | 6983.0452 | 0 | 0 | 0 | 0 | [5 empty] | 7205.5534 |  | 6948.7269 |  | 6988.683 |  | 7047.6544
| Chlorine | µg/dscm |  | 964.0056 | 100 | 221.2154 | 100 | 216.6397 | 31.2339 | 467.2869 | 100 | 2215.9608 | 100 | 2251.192 | 100 | 2255.6011 | 100 | 2240.918 | 0 | 0 | 0 | 0 |  |  |  |  | 69.685 | 3179.9664 | 100 | 2472.4073 | 100 | 2472.2407 | 82.7455 | 2708.2048
| Antimony | µg/dscm | 100 | 125.1955 | 100 | 130.1267 | 100 | 127.4351 | 100 | 127.5858 | 100 | 438.1843 | 100 | 455.4435 | 100 | 446.0228 | 100 | 446.5502 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 563.3799 | 100 | 585.5702 | 100 | 573.4579 | 100 | 574.136
| Arsenic | µg/dscm | 100 | 25.0391 | 100 | 26.0253 | 100 | 25.487 | 100 | 25.5172 | 100 | 75.1173 | 100 | 78.076 | 100 | 76.4611 | 100 | 76.5515 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 100.1564 | 100 | 104.1014 | 100 | 101.9481 | 100 | 102.0686
| Barium | µg/dscm | 100 | 25.0391 | 100 | 26.0253 | 100 | 25.487 | 100 | 25.5172 |  | 20744.8989 |  | 21822.248 |  | 21217.9423 |  | 21261.6964 | 0 | 0 | 0 | 0 | [5 empty] | 20769.938 |  | 21848.2733 |  | 21243.4293 |  | 21287.2135
| Beryllium | µg/dscm | 100 | 0 | 100 | 0 | 100 | 0 | 100 | 0 |  | 25.0391 |  | 26.0253 |  | 25.487 |  | 25.5172 | 0 | 0 | 0 | 0 | [5 empty] | 25.0391 |  | 26.0253 |  | 25.487 |  | 25.5172
| Cadmium | µg/dscm | 100 | 12.5196 | 100 | 13.0127 | 100 | 12.7435 | 100 | 12.7586 | 100 | 37.5587 | 100 | 39.038 | 100 | 38.2305 | 100 | 38.2757 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 50.0782 | 100 | 52.0507 | 100 | 50.974 | 100 | 51.0343
| Chromium | µg/dscm |  | 813.7709 |  | 1210.1783 |  | 1095.9418 |  | 1039.9637 |  | 237.8715 |  | 130.1267 |  | 114.6916 |  | 160.8966 | 5133.0166 | 5100.9667 | 2523.2148 | 4252.0058 | [5 empty] | 6184.659 |  | 6441.2718 |  | 3733.8481 |  | 5452.8661
| Lead | µg/dscm | 100 | 12.5196 |  | 13.0127 | 100 | 12.7435 | 66.0028 | 12.7586 | 100 | 363.067 | 100 | 377.3674 | 100 | 382.3053 | 100 | 374.2466 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 375.5866 | 100 | 390.3801 | 100 | 395.0488 | 100 | 387.0052
| Mercury | µg/dscm | 100 | 0.69615 | 100 | 0.74805 | 100 | 0.72669 | 100 | 0.72363 | 100 | 2.4367 | 100 | 2.4829 | 100 | 2.4837 | 100 | 2.4678 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 3.1329 | 100 | 3.2309 | 100 | 3.2104 | 100 | 3.1914
| Nickel | µg/dscm |  | 212.8324 |  | 494.4815 |  | 280.3572 |  | 329.2237 | 100 | 300.4693 | 100 | 299.2914 | 100 | 305.8442 | 100 | 301.8683 | 0 | 0 | 0 | 0 |  |  |  |  | 58.5366 | 513.3017 | 37.7049 | 793.7729 | 52.1739 | 586.2014 | 47.8327 | 631.092
| Selenium | µg/dscm | 100 | 12.5196 | 100 | 13.0127 | 100 | 12.7435 | 100 | 12.7586 |  | 125.1955 |  | 156.152 |  | 216.6397 |  | 165.9957 | 0 | 0 | 0 | 0 | [5 empty] | 137.7151 |  | 169.1647 |  | 229.3832 |  | 178.7543
| Silver | µg/dscm | 100 | 25.0391 | 100 | 26.0253 | 100 | 25.487 | 100 | 25.5172 | 100 | 75.1173 | 100 | 78.076 | 100 | 76.4611 | 100 | 76.5515 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 100.1564 | 100 | 104.1014 | 100 | 101.9481 | 100 | 102.0686
| Thallium | µg/dscm | 100 | 25.0391 | 100 | 26.0253 | 100 | 25.487 | 100 | 25.5172 | 100 | 75.1173 | 100 | 78.076 | 100 | 76.4611 | 100 | 76.5515 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 100.1564 | 100 | 104.1014 | 100 | 101.9481 | 100 | 102.0686
| Zinc | µg/dscm | 100 | 37.5587 | 100 | 39.038 | 100 | 38.2305 | 100 | 38.2757 |  | 813.7709 |  | 624.6082 |  | 573.4579 |  | 670.6123 | 0 | 0 | 0 | 0 | [5 empty] | 851.3296 |  | 663.6462 |  | 611.6884 |  | 708.8881
| SVM | µg/dscm | 100 | 25.0391 | 50 | 26.0253 | 100 | 12.7435 | 100 | 21.2693 | 100 | 400.6257 | 100 | 416.4054 | 100 | 420.5358 | 100 | 412.5223 | [8 empty] | 100 | 425.6648 | 97.0588 | 442.4308 | 100 | 433.2793 | 100 | 433.7916
| LVM | µg/dscm | 2.6667 | 938.9665 | 1.9417 | 1340.305 | 2.0833 | 1223.3769 | 2.1855 | 1167.5494 | 29.6296 | 338.0279 | 44.4444 | 234.2281 | 47.0588 | 216.6397 | 38.8145 | 262.9652 | 5133.0166 | 5100.9667 | 2523.2148 | 4252.0058 |  |  |  |  | 1.9531 | 6410.011 | 1.9493 | 6675.4998 | 3.2154 | 3963.2313 | 2.2452 | 5682.5204
* | 1014C11 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Coal |  | Coal |  | Coal |  | Coal
| Feedstream Description |  |  | Waste |  | Waste |  | Waste |  | Waste |  | Coal |  | Coal |  | Coal |  | Coal
| Feed Rate | lb/hr |  | 8500 |  | 8500 |  | 8490 |  | 8496.6667 |  | 55680 |  | 56060 |  | 56040 |  | 55926.6667

## process
Process Information
1014C10 |  | R1 | R2 | R3
Comb Chamb Temp | °F | 1461.6 | 1470.2 | 1476.5
Steam Production Rate | M lb/hr | 744.96 | 735.19 | 747.22
Baghouse Temp | °F | 383.49 | 387.75 | 385.76
1014C11 |  | R1 | R2 | R3
Comb Chamb Temp | °F | 1099.2 | 1092.5 | 1102.3
Steam Production Rate | M lb/hr | 638.25 | 642.11 | 641.75
Baghouse Temp | °F | 336.41 | 330.2 | 326.91