## list
source
cond
emiss
feed
df c4

## source
Source Description
Phase II ID No. | 2013
EPA ID No. | TXD008123317
Facility Name | E.I. Du Pont De Nemours & Company, Inc.
Facility Location
City | Victoria
State | TX
Unit ID Name/No. | Boiler Nos. 3 & 4
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics
Capacity (MMBtu/hr) | 1000
Soot Blowing | None
APCS Detailed Acronym
APCS General Class
APCS Characteristics
Hazardous Wastes | Liq
Haz Waste Description | Liquid wastes
Supplemental Fuel | ?
Stack Characteristics
Diameter (ft) | 13.6667
Height (ft) | 150
Gas Velocity (ft/sec) | 50
Gas Temperature (°F) | 506
Permitting Status | Tier I for metals, Cl (except Cr+6 Tier III)
HWC Burn Status (Date if Terminated)

## cond
Cond Description
2013C1
Report Name/Date | Source Emission Survey of E.I. Du Pont De Nemours & Company, Inc. Boiler 3 and 4 Stack, June 1995
Report Prepare | METCO Env
Testing Firm | METCO Env
Testing Dates | June 26-27, 1995
Cond Dates | 1995-06-01
Condition Descr | CoC
Content | PM, Cr+6/Cr
2013C2
Report Name/Date | Source Emission Survey of E.I. Du Pont De Nemours & Company, Inc. Boiler 3 and 4 Stack, June 1995
Report Prepare | METCO Env
Testing Firm | METCO Env
Testing Dates | June 27-28, 1995
Cond Dates | 1995-06-01
Condition Descr | CoC
Content | PM, Cr+6/Cr
2013C3
Report Name/Date | Dupont DRE Burn, Boiler No. 3 Stack, Victoria, TX, Feb. 1999
Report Prepare | METCO Env
Testing Firm | METCO Env
Testing Dates | February 15-16, 1999
Cond Dates | 1999-02-01
Condition Descr | Trial burn; DRE
Content | Monochlorobenzene DRE
2013C4
Report Name/Date | Dupont Risk Burn, Boiler No. 3 Stack, Victoria, TX, Feb. 1999
Report Prepare | METCO Env
Testing Firm | METCO Env
Testing Dates | February 8-12, 1999
Cond Dates | 1999-02-01
Condition Descr | Risk burn, normal op cond w/ Cr spike
Content | PCDD/PCDF, PM, PSD, HCl/Cl2, Cr+6

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
1 | 2013C1 |  |  |  |  | R1 |  | R2 |  | R3 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0273 |  | 0.0444 |  | 0.0302 | 0.034
| Chromium |  | lb/hr |  |  | 0.101 |  | 0.112 |  | 0.071 | 0.094667
| Chromium (Hex) |  | lb/hr |  |  | 0.029 |  | 0.035 |  | 0.02 | 0.028
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  |  | 162567 |  | 168691 |  | 167774 | 166344
| O2 |  | % |  |  | 8.6 |  | 8.2 |  | 8 | 8.2667
| Moisture |  | % |  |  | 14.87 |  | 14.55 |  | 15.57 | 14.9967
| Temperature |  | °F |  |  | 504 |  | 507 |  | 497 | 502.6667
| Sampling Train | Cr/Cr+6 | E2
| Stack Gas Flowrate |  | dscfm |  |  | 166803 |  | 162826 |  | 161282 | 163637
| O2 |  | % |  |  | 8.6 |  | 8.2 |  | 8 | 8.2667
| Moisture |  | % |  |  | 11.22 |  | 13.95 |  | 15.73 | 13.6333
| Temperature |  | °F |  |  | 504 |  | 508 |  | 503 | 505
| Chromium | E2 | µg/dscm | y |  | 182.7856 |  | 201.1548 |  | 126.758 | 170.0669
| Chromium (Hex) | E2 | µg/dscm | y |  | 52.483 |  | 62.8609 |  | 35.7065 | 50.3015
| LVM | E2 | µg/dscm | y |  | 182.7856 |  | 201.1548 |  | 126.758 | 170.0669 | (Cr only)
2 | 2013C2 |  |  |  |  | R1 |  | R2 |  | R3 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0386 |  | 0.0208 |  | 0.0729 | 0.044
| Chromium |  | lb/hr |  |  | 0.064 |  | 0.085 |  | 0.333 | 0.16067
| Chromium (Hex) |  | lb/hr |  |  | 0.026 |  | 0.035 |  | 0.043 | 0.035
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  |  | 62068 |  | 64650 |  | 63185 | 63301
| O2 |  | % |  |  | 11.6 |  | 11.4 |  | 11.6 | 11.5333
| Moisture |  | % |  |  | 17.19 |  | 17.26 |  | 16.76 | 17.07
| Temperature |  | °F |  |  | 289 |  | 284 |  | 276 | 283
| Sampling Train | Cr/Cr+6 | E2
| Stack Gas Flowrate |  | dscfm |  |  | 67981 |  | 78911 |  | 65272 | 70721.3333
| O2 |  | % |  |  | 11.6 |  | 11.4 |  | 11.6 | 11.5333
| Moisture |  | % |  |  | 16.7 |  | 16.64 |  | 17.69 | 17.01
| Temperature |  | °F |  |  | 294 |  | 287 |  | 278 | 286.3333
| Chromium | E1 | µg/dscm | y |  | 374.896 |  | 420.0068 |  | 2031.5881 | 898.3063
| Chromium (Hex) | E1 | µg/dscm | y |  | 152.3015 |  | 172.944 |  | 262.3372 | 195.6891
| LVM | E1 | µg/dscm | y |  | 374.896 |  | 420.0068 |  | 2031.5881 | 898.3063
3 | 2013C3 |  |  |  |  | R1 |  | R2 |  | R3 | Cond Avg
| POHC DRE | Chlorobenzene
| POHC Feedrate |  | lb/hr |  |  | 160 |  | 160 |  | 160
Emissions Rate
| DRE | E1 | % |  | > | 99.998 | > | 99.998 | > | 99.998
| Sampling Train | POHC | E1
| Stack Gas Flowrate |  | dscfm |  |  | 163984 |  | 169132 |  | 165576 | 166230.6667
| O2 |  | % |  |  | 13.6 |  | 13.5 |  | 13.8 | 13.6333
| Moisture |  | % |  |  | 8.9 |  | 10.4 |  | 8.88 | 9.3933
| Temperature |  | °F |  |  | 318 |  | 314 |  | 314 | 315.3333
4 | 2013C4 |  |  |  |  | R1 |  | R2 |  | R3 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0088 |  | 0.0069 |  | 0.0076 | 0.0078
| HCl |  | ppmv | n |  | 16.3 |  | 10.1 |  | 11.8 | 12.7333
| Cl2 |  | ppmv | n |  | 0.02 |  | 0.02 |  | 0.01 | 0.016667
| Chromium (Hex) |  | µg/dscm | n |  | 118.6 |  | 161.5 |  | 138.5 | 139.5
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 213385 |  | 222830 |  | 225725 | 220646.6667
| O2 |  | % |  |  | 6.3 |  | 6.6 |  | 6.6 | 6.5
| Moisture |  | % |  |  | 18.2 |  | 17.6 |  | 16.3 | 17.3667
| Temperature |  | °F |  |  | 382 |  | 387 |  | 383 | 384
| Sampling Train | Cr+6 | E2
| Stack Gas Flowrate |  | dscfm |  |  | 228175 |  | 216511 |  | 227662 | 224116
| O2 |  | % |  |  | 6.3 |  | 6.6 |  | 6.6 | 6.5
| Moisture |  | % |  |  | 11.3 |  | 17.98 |  | 10.48 | 13.2533
| Temperature |  | °F |  |  | 385 |  | 391 |  | 381 | 385.6667
| HCl | E1 | ppmv | y |  | 15.5238 |  | 9.8194 |  | 11.4722 | 12.2943
| Cl2 | E1 | ppmv | y |  | 0.019048 |  | 0.019444 |  | 0.0097222 | 0.016092
| Total Chlorine | E1 | ppmv | y |  | 15.5619 |  | 9.8583 |  | 11.4917 | 12.3264
| Chromium (Hex) | E2 | µg/dscm | y |  | 112.9524 |  | 157.0139 |  | 134.6528 | 134.6897
| Particle Size Distribution | in microns
| Median Size |  | microns |  |  | 1.5 |  | 2.95 | < | 0.68
| <2 |  | % wt |  |  | 59.5 |  | 39 |  | 85.8
| <10 |  | % wt |  |  | 95.9 |  | 88.5 |  | 97.6

## feed
Feedstreams
* | 2013C1 |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Liq waste |  | Liq waste |  | Liq waste |  | Liq waste | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Ash |  | g/hr | nd | 5196.434 | nd | 5145.239 | nd | 17377.012 |  | 9239.562 | 6731.424 | 6731.424 | 6735.96 | 6732.936
| Chlorine |  | g/hr | nd | 7184.725 | nd | 6714.176 | nd | 6981.375 |  | 6960.092
| Antimony |  | g/hr | nd | 15.84 | nd | 15.675 | nd | 16.483 |  | 15.999
| Arsenic |  | g/hr | nd | 0.832 | nd | 0.824 | nd | 1.544 |  | 1.067
| Barium |  | g/hr | nd | 0.725 | nd | 0.839 | nd | 0.642 |  | 0.735
| Beryllium |  | g/hr | nd | 0.104 | nd | 0.103 | nd | 0.104 |  | 0.104
| Cadmium |  | g/hr | nd | 0.104 | nd | 0.103 | nd | 0.104 |  | 0.104
| Chromium |  | g/hr |  | 8.899 |  | 9.766 |  | 13.612 |  | 10.759 | 331.128 | 331.128 | 331.128 | 331.128
| Lead |  | g/hr | nd | 16.629 | nd | 18.445 | nd | 17.432 |  | 17.502
| Mercury |  | g/hr | nd | 0.104 | nd | 0.103 | nd | 0.104 |  | 0.104
| Silver |  | g/hr | nd | 2.608 | nd | 2.573 | nd | 2.61 |  | 2.597
| Thallium |  | g/hr | nd | 0.832 | nd | 1.605 | nd | 0.832 |  | 1.09
| Gas Flowrate |  | dscfm |  | 162567 |  | 168691 |  | 167774 |  | 166344 | 162567 | 168691 | 167774 | 166344 |  | 162567 |  | 168691 |  | 167774 |  | 166344
| Oxygen |  | % |  | 8.6 |  | 8.2 |  | 8 |  | 8.2667 | 8.6 | 8.2 | 8 | 8.2667 |  | 8.6 |  | 8.2 |  | 8 |  | 8.2667
| Thermal Feedrate |  | MMBtu/hr
| Estimated Firing Rate |  | MMBtu/hr | [13 empty] | 639.9463 |  | 685.4745 |  | 692.4006 |  | 672.417
Feedrate MTEC Calculations
| Ash |  | mg/dscm | 100 | 21.254 | 100 | 19.6469 | 100 | 65.6897 | 100 | 35.5302 | 27.5323 | 25.7037 | 25.4637 | 26.2087 | 43.5655 | 48.7864 | 43.3223 | 45.3506 | 72.065 | 91.1534 | 57.5491 | 61.7389
| Chlorine |  | ug/dscm | 100 | 29386.4025 | 100 | 25637.8256 | 100 | 26391.4532 | 100 | 27138.5604 |  |  |  |  | 100 | 29386.4025 | 100 | 25637.8256 | 100 | 26391.4532 | 100 | 27138.5604
| Antimony |  | ug/dscm | 100 | 64.7875 | 100 | 59.8544 | 100 | 62.3101 | 100 | 62.3173 |  |  |  |  | 100 | 64.7875 | 100 | 59.8544 | 100 | 62.3101 | 100 | 62.3173
| Arsenic |  | ug/dscm | 100 | 3.403 | 100 | 3.1464 | 100 | 5.8367 | 100 | 4.1287 |  |  |  |  | 100 | 3.403 | 100 | 3.1464 | 100 | 5.8367 | 100 | 4.1287
| Barium |  | ug/dscm | 100 | 2.9653 | 100 | 3.2037 | 100 | 2.4269 | 100 | 2.8653 |  |  |  |  | 100 | 2.9653 | 100 | 3.2037 | 100 | 2.4269 | 100 | 2.8653
| Beryllium |  | ug/dscm | 100 | 0.42537 | 100 | 0.3933 | 100 | 0.39315 | 100 | 0.40394 |  |  |  |  | 100 | 0.42537 | 100 | 0.3933 | 100 | 0.39315 | 100 | 0.40394
| Cadmium |  | ug/dscm | 100 | 0.42537 | 100 | 0.3933 | 100 | 0.39315 | 100 | 0.40394 |  |  |  |  | 100 | 0.42537 | 100 | 0.3933 | 100 | 0.39315 | 100 | 0.40394
| Chromium |  | ug/dscm |  | 36.398 |  | 37.2911 |  | 51.457 |  | 41.7154 | 1354.354 | 1264.3997 | 1251.7519 | 1288.9528 |  | 1390.7519 |  | 1301.6908 |  | 1303.2088 |  | 1330.6681
| Lead |  | ug/dscm | 100 | 68.0146 | 100 | 70.4315 | 100 | 65.8976 | 100 | 68.1146 |  |  |  |  | 100 | 68.0146 | 100 | 70.4315 | 100 | 65.8976 | 100 | 68.1146
| Mercury |  | ug/dscm | 100 | 0.42537 | 100 | 0.3933 | 100 | 0.39315 | 100 | 0.40394 |  |  |  |  | 100 | 0.42537 | 100 | 0.3933 | 100 | 0.39315 | 100 | 0.40394
| Silver |  | ug/dscm | 100 | 10.667 | 100 | 9.8249 | 100 | 9.8665 | 100 | 10.1195 |  |  |  |  | 100 | 10.667 | 100 | 9.8249 | 100 | 9.8665 | 100 | 10.1195
| Thallium |  | ug/dscm | 100 | 3.403 | 100 | 6.1286 | 100 | 3.1452 | 100 | 4.2256 |  |  |  |  | 100 | 3.403 | 100 | 6.1286 | 100 | 3.1452 | 100 | 4.2256
| SVM |  | ug/dscm | 100 | 68.44 | 100 | 35.4124 | 100 | 33.1454 | 100 | 45.6659 |  |  |  |  | 100 | 68.44 | 100 | 35.4124 | 100 | 33.1454 | 100 | 45.6659
| LVM |  | ug/dscm | 9.517 | 40.2264 | 8.6692 | 40.8308 | 10.7995 | 57.6869 | 9.8007 | 46.248 | 1354.354 | 1264.3997 | 1251.7519 | 1288.9528 |  | 1394.5803 |  | 1305.2305 |  | 1309.4387 |  | 1335.2008
* | 2013C2 |  |  |  | R1 |  | F2 |  | F3 |  | Cond Avg | R1 | F2 | F3 | Cond Avg |  | R1 |  | F2 |  | F3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Liq waste |  | Liq waste |  | Liq waste |  | Liq waste | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Ash |  | g/hr | nd | 1292.023 | nd | 1806.844 | nd | 1671.498 |  | 1590.122 | 3365.712 | 3365.712 | 3370.248 | 3367.224
| Chlorine |  | g/hr | nd | 3245.56 | nd | 2855.665 | nd | 2202.663 |  | 2767.963
| Antimony |  | g/hr | nd | 4.091 | nd | 3.635 | nd | 3.542 |  | 3.756
| Arsenic |  | g/hr | nd | 0.207 | nd | 0.184 | nd | 0.187 |  | 0.193
| Barium |  | g/hr | nd | 0.261 |  | 0.257 | nd | 0.21 |  | 0.243
| Beryllium |  | g/hr | nd | 0.025 | nd | 0.023 | nd | 0.023 |  | 0.024
| Cadmium |  | g/hr |  | 0.025 | nd | 0.028 | nd | 0.023 |  | 0.025
| Chromium |  | g/hr |  | 2.697 |  | 1.846 |  | 2.017 |  | 2.187 | 331.128 | 331.128 | 331.128 | 331.128
| Lead |  | g/hr | nd | 4.178 | nd | 3.931 | nd | 3.723 |  | 3.944
| Mercury |  | g/hr | nd | 0.025 | nd | 0.023 | nd | 0.023 |  | 0.024
| Silver |  | g/hr | nd | 0.651 | nd | 1.07 | nd | 0.679 |  | 0.8
| Thallium |  | g/hr | nd | 0.26 | nd | 0.475 | nd | 0.51 |  | 0.415
| Gas Flowrate |  | dscfm |  | 62068 |  | 64650 |  | 63185 |  | 63301 | 62068 | 64650 | 63185 | 63301 |  | 62068 |  | 64650 |  | 63185 |  | 63301
| Oxygen |  | % |  | 11.6 |  | 11.4 |  | 11.6 |  | 11.5333 | 11.6 | 11.4 | 11.6 | 11.5333 |  | 11.6 |  | 11.4 |  | 11.6 |  | 11.5333
| Estimated Firing Rate |  | MMBtu/hr | [13 empty] | 185.2188 |  | 197.0286 |  | 188.5521 |  | 190.2379
Feedrate MTEC Calculations
| Ash |  | mg/dscm | 100 | 18.2585 | 100 | 24.0033 | 100 | 23.2035 | 100 | 21.8218 | 47.5633 | 44.7124 | 46.7854 | 46.3292 | 27.7393 | 65.8218 | 34.9314 | 68.7157 | 33.1532 | 69.9889 | 32.0198 | 68.151
| Chlorine |  | ug/dscm | 100 | 45865.3157 | 100 | 37936.5512 | 100 | 30577.119 | 100 | 38126.3286 |  |  |  |  | 100 | 45865.3157 | 100 | 37936.5512 | 100 | 30577.119 | 100 | 38126.3286
| Antimony |  | ug/dscm | 100 | 57.8128 | 100 | 48.2898 | 100 | 49.1696 | 100 | 51.7574 |  |  |  |  | 100 | 57.8128 | 100 | 48.2898 | 100 | 49.1696 | 100 | 51.7574
| Arsenic |  | ug/dscm | 100 | 2.9253 | 100 | 2.4444 | 100 | 2.5959 | 100 | 2.6552 |  |  |  |  | 100 | 2.9253 | 100 | 2.4444 | 100 | 2.5959 | 100 | 2.6552
| Barium |  | ug/dscm | 100 | 3.6884 |  | 3.4142 | 100 | 2.9152 | 65.9188 | 3.3392 |  |  |  |  | 100 | 3.6884 | 100 | 3.4142 | 100 | 2.9152 | 100 | 3.3392
| Beryllium |  | ug/dscm | 100 | 0.35329 | 100 | 0.30555 | 100 | 0.31928 | 100 | 0.32604 |  |  |  |  | 100 | 0.35329 | 100 | 0.30555 | 100 | 0.31928 | 100 | 0.32604
| Cadmium |  | ug/dscm |  | 0.35329 | 100 | 0.37197 | 100 | 0.31928 | 66.1774 | 0.34818 |  |  |  |  | 100 | 0.35329 | 100 | 0.37197 | 100 | 0.31928 | 100 | 0.34818
| Chromium |  | ug/dscm |  | 38.1132 |  | 24.5235 |  | 27.9998 |  | 30.2122 | 4679.4052 | 4398.9244 | 4596.6815 | 4558.337 |  | 4717.5184 |  | 4423.4478 |  | 4624.6813 |  | 4588.5492
| Lead |  | ug/dscm | 100 | 59.0423 | 100 | 52.222 | 100 | 51.6823 | 100 | 54.3155 |  |  |  |  | 100 | 59.0423 | 100 | 52.222 | 100 | 51.6823 | 100 | 54.3155
| Mercury |  | ug/dscm | 100 | 0.35329 | 100 | 0.30555 | 100 | 0.31928 | 100 | 0.32604 |  |  |  |  | 100 | 0.35329 | 100 | 0.30555 | 100 | 0.31928 | 100 | 0.32604
| Silver |  | ug/dscm | 100 | 9.1997 | 100 | 14.2146 | 100 | 9.4258 | 100 | 10.9467 |  |  |  |  | 100 | 9.1997 | 100 | 14.2146 | 100 | 9.4258 | 100 | 10.9467
| Thallium |  | ug/dscm | 100 | 3.6742 | 100 | 6.3102 | 100 | 7.0798 | 100 | 5.6881 |  |  |  |  | 100 | 3.6742 | 100 | 6.3102 | 100 | 7.0798 | 100 | 5.6881
| SVM |  | ug/dscm | 0.99405 | 59.3956 | 100 | 52.594 | 100 | 52.0015 | 99.7846 | 54.6637 |  |  |  |  | 100 | 59.3956 | 100 | 52.594 | 100 | 52.0015 | 100 | 54.6637
| LVM |  | ug/dscm | 7.9208 | 41.3918 | 10.0828 | 27.2734 | 9.4297 | 30.915 | 8.9814 | 33.1934 | 4679.4052 | 4398.9244 | 4596.6815 | 4558.337 |  | 4720.797 |  | 4426.1978 |  | 4627.5965 |  | 4591.5304
* | 2013C3
| Gas Flowrate |  | dscfm |  | 163984 |  | 169132 |  | 165576 |  | 166230.6667
| Oxygen |  | % |  | 13.6 |  | 13.5 |  | 13.8 |  | 13.6333
| Estimated Firing Rate |  | MMBtu/hr | [7 empty] | 388.7511
* | 2013C4 |  |  |  | Cond Avg |  | Cond Avg |  | Cond Avg |  | Cond Avg | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F2 |  | F3 |  | F4 | F5
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike
| Feedstream Description |  |  |  | NVR Waste |  | ADN/LBW |  | C12 WFE |  | A Waste Oil | Spike
| Density |  | g/mL |  | 1.05 |  | 0.81 |  | 0.93 |  | 1
| Viscosity |  | cSt |  | 32.7 |  | 0.65 |  | 164.5 |  | 0.91
| Heating Value |  | Btu/lb |  | 9616 |  | 15169 |  | 18666 |  | 84
| Ash |  | wt % | nd | 0.1 | nd | 0.1 |  | 0.8 | nd | 0.1
| Chlorine |  | ppmw | nd | 22 | nd | 25 |  | 1.27 |  | 61
| Chromium |  | lb/hr | [8 empty] | 0.76
| Antimony |  | ppmw | nd | 0.2 | nd | 0.2 | nd | 0.2 | nd | 0.2
| Arsenic |  | ppmw | nd | 0.02 | nd | 0.01 | nd | 0.02 | nd | 0.02
| Barium |  | ppmw | nd | 0.02 | nd | 0.01 | nd | 0.01 |  | 0.45
| Beryllium |  | ppmw | nd | 0.01 | nd | 0.01 | nd | 0.01 | nd | 0.01
| Cadmium |  | ppmw | nd | 0.02 | nd | 0.01 | nd | 0.01 | nd | 0.01
| Chromium |  | ppmw |  | 4.4 |  | 0.27 |  | 0.26 |  | 0.26
| Cobalt |  | ppmw |  | 48.7 | nd | 10 | nd | 10 | nd | 10
| Lead |  | ppmw | nd | 0.051 | nd | 0.01 | nd | 0.011 | nd | 0.011
| Manganese |  | ppmw | nd | 3 | nd | 3 | nd | 3 | nd | 3
| Mercury |  | ppmw | nd | 0.04 | nd | 0.04 | nd | 0.04 | nd | 0.04
| Molybdenum |  | ppmw | nd | 8 | nd | 8 | nd | 8 | nd | 8
| Nickel |  | ppmw |  | 1 |  | 0.34 | nd | 0.06 |  | 0.24
| Selenium |  | ppmw | nd | 0.025 | nd | 0.02 | nd | 0.025 | nd | 0.02
| Silver |  | ppmw | nd | 0.02 | nd | 0.01 | nd | 0.01 | nd | 0.01
| Thallium |  | ppmw | nd | 0.01 | nd | 0.01 | nd | 0.01 | nd | 0.01
| Vanadium |  | ppmw | nd | 10 | nd | 10 | nd | 10 | nd | 10
| Stack Gas Flowrate |  | dscfm |  | 220646.6667 |  | 220646.6667 |  | 220646.6667 |  | 220646.6667 | 220646.6667
| Oxygen |  | % |  | 6.5 |  | 6.5 |  | 6.5 |  | 6.5 | 6.5
can't calculate; need feedrates of waste
| Thermal Feedrate |  | MMBtu/hr
| Estimated Firing Rate |  | MMBtu/hr | [8 empty] | 1015.6751
| Ash |  | mg/dscm | nd
| Chlorine |  | ug/dscm | nd
| Chromium |  | ug/dscm
| Antimony |  | ug/dscm | nd
| Arsenic |  | ug/dscm | nd
| Barium |  | ug/dscm | nd
| Beryllium |  | ug/dscm | nd
| Cadmium |  | ug/dscm | nd
| Chromium |  | ug/dscm
| Cobalt |  | ug/dscm
| Lead |  | ug/dscm | nd
| Manganese |  | ug/dscm | nd
| Mercury |  | ug/dscm | nd
| Molybdenum |  | ug/dscm | nd
| Nickel |  | ug/dscm
| Selenium |  | ug/dscm | nd
| Silver |  | ug/dscm | nd
| Thallium |  | ug/dscm | nd
| Vanadium |  | ug/dscm | nd

## df c4
PCDD/PCDF
N
Facility Name and ID: |  | DuPont, Victoria, TX, Boiler Nos. 3 and 4
Condition ID: |  | 2013C4
Condition/Test Date: |  | Risk burn, normal conditions, February, 1999
|  | I-TEF |  | Run 1 |  |  |  |  | Run 2 |  |  |  |  | Run 4
|  | Wght Fact |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ
|  |  |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND
Stack Gas ng/dscm @ 7% O2
| 2,3,7,8-TCDD | 1 |  | 0.002 | 0.002 | 0.002 | 0.002 |  | 0.001 | 0.001 | 0.001 | 0.001 | nd | 0.001 | 0.001 | 0.0005 | 0.0005
| TCDD Total | 0 |  | 0.034 | 0 | 0.034 | 0 |  | 0.033 | 0 | 0.033 | 0 |  | 0.003 | 0 | 0.003 | 0
| 1,2,3,7,8-PCDD | 0.5 |  | 0.005 | 0.0025 | 0.005 | 0.0025 |  | 0.005 | 0.0025 | 0.005 | 0.0025 | nd | 0.001 | 0.0005 | 0.0005 | 0.00025
| PCDD Total | 0 |  | 0.051 | 0 | 0.051 | 0 |  | 0.048 | 0 | 0.048 | 0 |  | 0.005 | 0 | 0.005 | 0
| 1,2,3,4,7,8-HxCDD | 0.1 |  | 0.005 | 0.0005 | 0.005 | 0.0005 |  | 0.004 | 0.0004 | 0.004 | 0.0004 | nd | 0.002 | 0.0002 | 0.001 | 0.0001
| 1,2,3,6,7,8-HxCDD | 0.1 |  | 0.004 | 0.0004 | 0.004 | 0.0004 |  | 0.006 | 0.0006 | 0.006 | 0.0006 | nd | 0.002 | 0.0002 | 0.001 | 0.0001
| 1,2,3,7,8,9-HxCDD | 0.1 |  | 0.003 | 0.0003 | 0.003 | 0.0003 |  | 0.003 | 0.0003 | 0.003 | 0.0003 | nd | 0.002 | 0.0002 | 0.001 | 0.0001
| HxCDD Total | 0 |  | 0.047 | 0 | 0.047 | 0 |  | 0.045 | 0 | 0.045 | 0 |  | 0.006 | 0 | 0.006 | 0
| 1,2,3,4,6,7,8-HpCDD | 0.01 |  | 0.014 | 0.00014 | 0.014 | 0.00014 |  | 0.017 | 0.00017 | 0.017 | 0.00017 |  | 0.004 | 4e-05 | 0.004 | 4e-05
| HpCDD Total | 0 |  | 0.025 | 0 | 0.025 | 0 |  | 0.028 | 0 | 0.028 | 0 |  | 0.006 | 0 | 0.006 | 0
| OCDD | 0.001 |  | 0.015 | 1.5e-05 | 0.015 | 1.5e-05 |  | 0.016 | 1.6e-05 | 0.016 | 1.6e-05 |  | 0.007 | 7e-06 | 0.007 | 7e-06
| 2,3,7,8-TCDF | 0.1 |  | 0.021 | 0.0021 | 0.021 | 0.0021 |  | 0.017 | 0.0017 | 0.017 | 0.0017 |  | 0.002 | 0.0002 | 0.002 | 0.0002
| TCDF Total | 0 |  | 0.67 | 0 | 0.67 | 0 |  | 0.527 | 0 | 0.527 | 0 |  | 0.064 | 0 | 0.064 | 0
| 1,2,3,7,8-PCDF | 0.05 |  | 0.031 | 0.00155 | 0.031 | 0.00155 |  | 0.025 | 0.00125 | 0.025 | 0.00125 |  | 0.004 | 0.0002 | 0.004 | 0.0002
| 2,3,4,7,8-PCDF | 0.5 |  | 0.047 | 0.0235 | 0.047 | 0.0235 |  | 0.038 | 0.019 | 0.038 | 0.019 |  | 0.006 | 0.003 | 0.006 | 0.003
| PCDF Total | 0 |  | 0.536 | 0 | 0.536 | 0 |  | 0.477 | 0 | 0.477 | 0 |  | 0.073 | 0 | 0.073 | 0
| 1,2,3,4,7,8-HxCDF | 0.1 |  | 0.038 | 0.0038 | 0.038 | 0.0038 |  | 0.035 | 0.0035 | 0.035 | 0.0035 |  | 0.007 | 0.0007 | 0.007 | 0.0007
| 1,2,3,6,7,8-HxCDF | 0.1 |  | 0.034 | 0.0034 | 0.034 | 0.0034 |  | 0.033 | 0.0033 | 0.033 | 0.0033 |  | 0.005 | 0.0005 | 0.005 | 0.0005
| 2,3,4,6,7,8-HxCDF | 0.1 |  | 0.045 | 0.0045 | 0.045 | 0.0045 |  | 0.038 | 0.0038 | 0.038 | 0.0038 |  | 0.007 | 0.0007 | 0.007 | 0.0007
| 1,2,3,7,8,9-HxCDF | 0.1 |  | 0.019 | 0.0019 | 0.019 | 0.0019 |  | 0.017 | 0.0017 | 0.017 | 0.0017 |  | 0.004 | 0.0004 | 0.004 | 0.0004
| HxCDF Total | 0 |  | 0.358 | 0 | 0.358 | 0 |  | 0.326 | 0 | 0.326 | 0 |  | 0.062 | 0 | 0.062 | 0
| 1,2,3,4,6,7,8-HpCDF | 0.01 |  | 0.042 | 0.00042 | 0.042 | 0.00042 |  | 0.043 | 0.00043 | 0.043 | 0.00043 |  | 0.011 | 0.00011 | 0.011 | 0.00011
| 1,2,3,4,7,8,9-HpCDF | 0.01 |  | 0.021 | 0.00021 | 0.021 | 0.00021 |  | 0.023 | 0.00023 | 0.023 | 0.00023 |  | 0.005 | 5e-05 | 0.005 | 5e-05
| HpCDF Total | 0 |  | 0.107 | 0 | 0.107 | 0 |  | 0.108 | 0 | 0.108 | 0 |  | 0.02 | 0 | 0.02 | 0
| OCDF | 0.001 |  | 0.007 | 7e-06 | 0.007 | 7e-06 |  | 0.011 | 1.1e-05 | 0.011 | 1.1e-05 |  | 0.006 | 6e-06 | 0.006 | 6e-06
| PCDD/PCDF (ng/dscm @ 7% O2) |  | 0 |  | 0.047242 | 1.85 | 0.047242 | 0 |  | 0.039907 | 1.619 | 0.039907 | 26.2074 |  | 0.008013 | 0.252 | 0.006963
| TEQ Cond Avg | 0.031371
| Total Cond Avg | 1.2403