## source
Source Description
Phase II ID No. | 2019
EPA ID No. | LAD008161234
Facility Name | Rhodia (formerly Rhone-Poulenc Basic Chemical Co.)
Facility Location
City | Baton Rouge
State | LA
Unit ID Name/No. | Unit 2
Other Sister Facilities | ?
Combustor | Sulfur Acid Recovery Unit
Combustor Characteristics
Capacity (MMBtu/hr) | 250
Soot Blowing
APCS | WESP
APCS Characteristics | Wet ESP
Hazardous Wastes | Liq
Haz Waste Description | Viscous liquid fuel
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft)
Height (ft)
Gas Velocity (ft/sec) | 17
Gas Temperature (°F) | 93
Permitting Status
HWC Burn Status (Date if Terminated)

## cond
Cond Description
2019C1
Report Name/Date | Trial Burn Results, October 1989
Report Prepare | Rohne-Poulenc Basic Chemical Co.
Testing Firm | Preiser Laboratories
Testing Dates | 1989-10-30
Condition Descr | Trial burn; max feedrate
Content | PM, CO, HC, HCl, DRE, NOx, SO2, PICs

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
1 | 2019C1 |  |  |  | R1 |  | R2 |  | R3 | Cond Avg
| PM |  | lb/hr |  | 1.56 |  | 1.83 |  | 1.26
| PM |  | mg/dscm | n | 3.61 |  | 4.11 |  | 3.2
| PM |  | gr/dscf | y | 0.0019227 |  | 0.0021045 |  | 0.0015356 | 0.0018543
| HCl |  | mg/dscm | n | 0.42 |  | 0.34 |  | 0.41
| HC (RA) |  | ppmv | n | 0.13 |  | 0.2 |  | 0.6
| CO (RA) |  | ppmv | n | 67.3 |  | 40.1 |  | 36.1
| SO2 |  | ppmv | n | 1460 |  | 1450 |  | 1510
| NOx |  | ppmv | n | 12.6 |  | 12.8 |  | 13.9
| H2SO4 |  | ppmv | n
| (Stack Gas Flowrate) |  | dscfm |  | 115540.8514 |  | 119049.4614 |  | 105278.2686 | 113289.5271
| Oxygen |  | % |  | 9.53 |  | 9.07 |  | 8.27 | 8.9567
| HCl |  | ppmv | y | 0.28048 |  | 0.22705 |  | 0.2738 | 0.26044
| Total Chlorine | Assumed that HCl train captures Cl2 as well | ppmv | y | 0.28048 |  | 0.22705 |  | 0.2738 | 0.26044
| HC (RA) |  | ppmv | y | 0.15867 |  | 0.2347 |  | 0.65986 | 0.35108
| CO (RA) |  | ppmv | y | 82.1447 |  | 47.0578 |  | 39.7015 | 56.3014
POHCs
| POHC DRE | CCl4
| POHC Feedrate |  | lb/hr |  | 5.25 |  | 6.98 |  | 7.21
| Emission Rate |  | lb/hr |  | 1.9e-05 |  | 2.8e-05 |  | 2.8e-05
| DRE |  | % |  | 100 |  | 100 |  | 100
| POHC DRE | C2H3Cl3
| POHC Feedrate |  | lb/hr |  | 4.5 |  | 5 |  | 4.6
| Emission Rate |  | lb/hr |  | 2.5e-05 |  | 2.6e-05 |  | 2.9e-05
| DRE |  | % |  | 100 |  | 100 |  | 100
| POHC DRE | Toluene
| POHC Feedrate |  | lb/hr |  | 4.5 |  | 5.4 |  | 5.48
| Emission Rate |  | lb/hr |  | 9.8e-05 |  | 8.9e-05 |  | 0.00013
| DRE |  | % |  | 100 |  | 100 |  | 100
| POHC DRE | C6H6
| POHC Feedrate |  | lb/hr
| Emission Rate |  | lb/hr |  | 0.00046 |  | 0.0007 |  | 0.00027
| DRE |  | %
PICs
| Unknown (m/z 46) |  | lb/hr |  | NA |  | ND |  | 0.0007
| Trichlorofluoromethane |  | lb/hr |  | NA | nd | 0.0036 | nd | 0.0035
| Unknown (m/z 59) |  | lb/hr |  | NA |  | ND |  | 0.001
| Carbon oxygen sulfide |  | lb/hr |  | NA |  | 0.00065 |  | ND
| Carbon disulfide |  | lb/hr |  | NA | nd | 0.036 | nd | 0.035
| Tetrachloroethylene |  | lb/hr |  | NA |  | 0.0004 |  | 3.5e-05
| Benzene |  | lb/hr |  | 0.0015 |  | 0.002 |  | 0.0007
| Methlcyclohexane |  | lb/hr |  | NA |  | ND |  | 7e-05
| C7 |  | lb/hr |  | NA |  | 0.002 |  | 0.0002
| C8 |  | lb/hr |  | NA |  | 0.003 |  | 0.0002
| C9 |  | lb/hr |  | NA |  | 0.003 |  | 0.0002
| C10 |  | lb/hr |  | NA | nd | 0.036 |  | 0.018
| C11 |  | lb/hr |  | NA |  | 0.022 |  | 0.0007
| Alkanes NOS |  | lb/hr |  | NA |  | 0.022 |  | 0.003
| Unknown (m/z 58) |  | lb/hr |  | NA |  | ND |  | 0.004
| C2 alkyl benzene |  | lb/hr |  | NA |  | ND |  | 0.0001
| Benzonitrile |  | lb/hr |  | NA |  | 0.0007 |  | 4e-05
| Benzaldehyde |  | lb/hr |  | NA |  | ND |  | 0.0002
| Trichlorobenzene |  | lb/hr |  | NA |  | ND |  | 4e-05
| Naphthalene |  | lb/hr |  | NA |  | ND |  | 4e-05
| MW 140 Unknown |  | lb/hr |  | NA |  | ND |  | 4e-05
| (m/z 57, 69, 111) |  | lb/hr |  | NA |  | ND |  | 4e-05

## feed
Feedstreams
* | 2019C1 |  | Cond Avg | Cond Avg | Cond Avg | Cond Avg | Total
| Feed Class 2 | [5 empty] | Total
| Feedstream Description |  | Synthetic Fuel | Viscous Fuel | Natural Gas | Spent Acid | Total
| Feed Rate | lb/min | 85 | 21.5
| Feed Rate | scfm |  |  | 200
| Feed Rate | gpm |  |  |  | 85
| Thermal Feedrate | M2Btu/hr |  |  | 12 |  | 245
| Ash | lb/min |  | 1.6 |  |  | 1.6
| Chlorine | lb/min | 10.4167 | 1.8667 |  |  | 12.2833
| Diesel | lb/min | 65
| Carbon Tet. | lb/min | 6.3
| 1,1,1 TCE | lb/min | 4.9
| Toluene | lb/min | 0.77 | 5.1
| Stack Gas Flowrate | dscfm |  |  |  |  | 113289.5271
| Oxygen | % |  |  |  |  | 8.9567
| Estimated Firing Rate | M2Btu/hr |  |  |  |  | 433.1376
Feedrate MTEC Calculations
| Ash | mg/dscm |  |  |  |  | 263.3789
| Chlorine | ug/dscm |  |  |  |  | 2021981.6954

## process
Process Information
Cond Avg
2019C1
Furnace Oxygen | % | 1.8
Furnace Temp | °F | 1700