## list
source
cond
emiss
feed

## source
Source Description
Phase II ID No. | 733
EPA ID No. | CAD009547050
Facility Name | Dow Chemical Co.
Facility Location
City | Torrance
State | CA
Unit ID Name/No. | U-305
Other Sister Facilities | U-304 (identical)
Number of Sister Facilities | 1
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid injection, process heater
Combustor Characteristics | Boiler -- Dowtherm process heater. 9.75 MM Btu/hr, Struthers Wells, 1979, Model No. 7CV 19-6PH, heats Dowtherm A liquid
Capacity (MMBtu/hr) | 9.8
Soot Blowing | None
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics | NA
Hazardous Wastes | Liq
Haz Waste Description | Liquid waste (D001, D018)
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 2.33
Height (ft) | 13.6
Gas Velocity (ft/sec) | 16.1967
Gas Temperature (°F) | 760
Permitting Status | Tier I metals and chlorine; Low Risk Waste Exemption (no PM, DRE for trial burn)
HWC Burn Status (Date if Terminated)

## cond
Cond Description
733C1
Report Name/Date | BIF Compliance Certification and Results of the Trial Burn for BIF Units U-304 and U-305; August 1992
Report Prepare | ENSR Consulting and Engineering
Testing Firm | ENSR Consulting and Engineering
Testing Dates | 1992-07-01
Cond Dates | 1992-07-01
Condition Descr | CoC; max waste feed
Content | PM, CO
733C2
Report Name/Date | BIF Compliance Certification and Results of the Trial Burn for BIF Units U-304 and U-305; August 1992
Report Prepare | ENSR Consulting and Engineering
Testing Firm | ENSR Consulting and Engineering
Testing Dates | July 2,1992
Cond Dates | 1992-07-01
Condition Descr | Trial burn, boiler load at 55%
Content | CO
733C3
Report Name/Date | BIF Compliance Certification and Results of the Trial Burn for BIF Units U-304 and U-305; August 1992
Report Prepare | ENSR Consulting and Engineering
Testing Firm | ENSR Consulting and Engineering
Testing Dates | July 2,1992
Cond Dates | 1992-07-01
Condition Descr | Trial burn, boiler load at 90%
Content | CO
733C4
Report Name/Date | BIF Compliance Certification and Results of the Trial Burn for BIF Units U-304 and U-305; August 1992
Report Prepare | ENSR Consulting and Engineering
Testing Firm | ENSR Consulting and Engineering
Testing Dates | July 2,1992
Cond Dates | 1992-07-01
Condition Descr | Trial burn, boiler load at 80%
Content | CO
733C5
Report Name/Date | BIF Compliance Certification and Results of the Trial Burn for BIF Units U-304 and U-305; August 1992
Report Prepare | ENSR Consulting and Engineering
Testing Firm | ENSR Consulting and Engineering
Testing Dates | July 2,1992
Cond Dates | 1992-07-01
Condition Descr | Trial burn, boiler load at 70%
Content | CO
733C6
Report Name/Date | BIF Compliance Certification and Results of the Trial Burn for BIF Units U-304 and U-305; August 1992
Report Prepare | ENSR Consulting and Engineering
Testing Firm | ENSR Consulting and Engineering
Testing Dates | July 2,1992
Cond Dates | 1992-07-01
Condition Descr | Trial burn, boiler load at 40%
Content | CO

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
1 | 733C1 | Coc Testing |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.002 | 0.0021 | 0.0013 | 0.0018
| CO (RA) | E1 | ppmv | y | 1.4 | 1.4 | 1.4 | 1.4
| CO (MHRA) | E1 | ppmv | y | 0 | 0 | 20.7 | 6.9
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 1859 | 1451 | 1497 | 1602.3333
| O2 |  | % |  | 4.5 | 5.1 | 4.4 | 4.6667
| Moisture |  | % |  | 11.3 | 10.7 | 10.6 | 10.8667
| Temperature |  | °F |  | 759 | 764 | 758 | 760.3333
2 | 733C2 | Trial Burn |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) |  | ppmv | y | 8.3 |  |  | 8.3
| Oxygen |  | % |  | 5.3 |  |  | 5.3
3 | 733C3 | Trial Burn |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) |  | ppmv | y | 1.4 |  |  | 1.4
| Oxygen |  | % |  | 4.5 |  |  | 4.5
4 | 733C4 | Trial Burn |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) |  | ppmv | y | 2.8 |  |  | 2.8
| Oxygen |  | % |  | 5.2 |  |  | 5.2
5 | 733C5 | Trial Burn |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) |  | ppmv | y | 1.4 |  |  | 1.4
| Oxygen |  | % |  | 4.7 |  |  | 4.7
6 | 733C6 | Trial Burn |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) |  | ppmv | y | 21.6 |  |  | 21.6
| Oxygen |  | % |  | 6.4 |  |  | 6.4

## feed
Feedstreams
* | 733C1 | CoC Testing |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Liq waste |  | Liq waste |  | Liq waste |  | Liq waste | Natural gas | Natural gas | Natural gas | Natural gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 240.8 |  | 242.8 |  | 237.2 |  | 240.3 | 118.2 | 118.6 | 122 | 119.6
| Thermal Feedrate |  | MMBtu/hr |  | 4.3 |  | 4.4 |  | 4.3 |  | 4.3 | 2.5 | 2.5 | 2.6 | 2.5 |  | 6.8 |  | 6.9 |  | 6.9 |  | 6.8
| Viscosity |  | SSU |  | 78.7 |  | 78.3 |  | 82.9 |  | 84.3
| Density |  | g/cc |  | 0.981 |  | 0.994 |  | 0.99 |  | 0.991
| Heating Value |  | Btu/lb |  | 18239 |  | 17928 |  | 17799 |  | 17990
| Ash |  | wt % | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Chlorine |  | ppmw |  | 113 |  | 62 |  | 143 |  | 131
| Antimony |  | ppmw | nd | 0.55 | nd | 0.51 | nd | 0.53 |  | 0.53
| Arsenic |  | ppmw | nd | 0.182 | nd | 0.171 | nd | 0.184 |  | 0.179
| Barium |  | ppmw |  | 0.383 |  | 0.145 |  | 0.455 |  | 0.313
| Beryllium |  | ppmw |  | 0.219 |  | 0.111 |  | 0.438 |  | 0.235
| Cadmium |  | ppmw | nd | 0.055 | nd | 0.026 | nd | 0.026 |  | 0.034
| Chromium |  | ppmw |  | 0.328 |  | 0.769 |  | 0.333 |  | 0.403
| Lead |  | ppmw | nd | 0.91 | nd | 0.43 | nd | 0.44 |  | 0.56
| Mercury |  | ppmw | nd | 0.1429 | nd | 0.1538 | nd | 0.1667 |  | 0.1492
| Silver |  | ppmw | nd | 0.18 | nd | 0.17 | nd | 0.18 |  | 0.18
| Thallium |  | ppmw | nd | 1.8 | nd | 0.85 | nd | 0.88 |  | 1.1
| Stack Gas Flowrate |  | dscfm |  | 1859 |  | 1451 |  | 1497 |  | 1602.3333 | [11 empty] | 1602.3333
| Oxygen |  | % |  | 4.5 |  | 5.1 |  | 4.4 |  | 4.6667 | [11 empty] | 4.6667
| Estimated Firing Rate |  | MMBtu/hr | [19 empty] | 8.3084
Feedrate MTEC Calculations
| Ash |  | mg/dscm | 100 | 29.3859 | 100 | 39.394 | 100 | 35.7298 | 100 | 34.8366 |  |  |  |  | 100 | 29.3859 | 100 | 39.394 | 100 | 35.7298 | 100 | 34.8366
| Chlorine |  | ug/dscm |  | 3320.6094 |  | 2442.4295 |  | 5109.3663 |  | 3624.1351 |  |  |  |  | 0 | 3320.6094 | 0 | 2442.4295 | 0 | 5109.3663 | 0 | 3624.1351
| Antimony |  | ug/dscm | 100 | 16.1623 | 100 | 20.091 | 100 | 18.9368 | 100 | 18.3967 |  |  |  |  | 100 | 16.1623 | 100 | 20.091 | 100 | 18.9368 | 100 | 18.3967
| Arsenic |  | ug/dscm | 100 | 5.3482 | 100 | 6.7364 | 100 | 6.5743 | 100 | 6.2196 |  |  |  |  | 100 | 5.3482 | 100 | 6.7364 | 100 | 6.5743 | 100 | 6.2196
| Barium |  | ug/dscm |  | 11.2548 |  | 5.7121 |  | 16.2571 |  | 11.0747 |  |  |  |  | 0 | 11.2548 | 0 | 5.7121 | 0 | 16.2571 | 0 | 11.0747
| Beryllium |  | ug/dscm |  | 6.4355 |  | 4.3727 |  | 15.6497 |  | 8.8193 |  |  |  |  | 0 | 6.4355 | 0 | 4.3727 | 0 | 15.6497 | 0 | 8.8193
| Cadmium |  | ug/dscm | 100 | 1.6162 | 100 | 1.0242 | 100 | 0.92898 | 100 | 1.1898 |  |  |  |  | 100 | 1.6162 | 100 | 1.0242 | 100 | 0.92898 | 100 | 1.1898
| Chromium |  | ug/dscm |  | 9.6386 |  | 30.294 |  | 11.898 |  | 17.2769 |  |  |  |  | 0 | 9.6386 | 0 | 30.294 | 0 | 11.898 | 0 | 17.2769
| Lead |  | ug/dscm | 100 | 26.7412 | 100 | 16.9394 | 100 | 15.7211 | 100 | 19.8006 |  |  |  |  | 100 | 26.7412 | 100 | 16.9394 | 100 | 15.7211 | 100 | 19.8006
| Mercury |  | ug/dscm | 100 | 4.1992 | 100 | 6.0588 | 100 | 5.9562 | 100 | 5.4047 |  |  |  |  | 100 | 4.1992 | 100 | 6.0588 | 100 | 5.9562 | 100 | 5.4047
| Silver |  | ug/dscm | 100 | 5.2895 | 100 | 6.697 | 100 | 6.4314 | 100 | 6.1393 |  |  |  |  | 100 | 5.2895 | 100 | 6.697 | 100 | 6.4314 | 100 | 6.1393
| Thallium |  | ug/dscm | 100 | 52.8947 | 100 | 33.4849 | 100 | 31.4423 | 100 | 39.2739 |  |  |  |  | 100 | 52.8947 | 100 | 33.4849 | 100 | 31.4423 | 100 | 39.2739
| SVM |  | ug/dscm | 100 | 28.3574 | 100 | 17.9637 | 100 | 16.6501 | 100 | 20.9904 |  |  |  |  | 100 | 28.3574 | 100 | 17.9637 | 100 | 16.6501 | 100 | 20.9904
| LVM |  | ug/dscm | 24.9657 | 21.4223 | 16.2702 | 41.4031 | 19.267 | 34.122 | 19.2464 | 32.3158 |  |  |  |  | 24.9657 | 21.4223 | 16.2702 | 41.4031 | 19.267 | 34.122 | 19.2464 | 32.3158
* | 733C2 | Trial Burn @ 55% Load |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  |  |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 |  |  |  | F2
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  |  |  | NG
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW |  |  |  | MF
| Feedstream Description |  |  |  | Liq waste |  | Liq waste |  | Liq waste |  | Liq waste |  |  |  | Natural gas
| Feed Rate |  | lb/hr |  | 120 |  | 120 |  | 120 |  | 120 |  |  |  | 156.8
| Thermal Feedrate |  | MMBtu/hr |  | 2.16 |  | 2.16 |  | 2.16 |  | 2.16 |  |  |  | 3.3
| Heating Value |  | Btu/lb |  | 17990 |  | 17990 |  | 17990 |  | 17990
* | 733C3 | Trial Burn @ 90% Load |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  |  |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 |  |  |  | F2
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  |  |  | NG
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW |  |  |  | MF
| Feedstream Description |  |  |  | Liq waste |  | Liq waste |  | Liq waste |  | Liq waste |  |  |  | Natural gas
| Feed Rate |  | lb/hr |  | 216 |  | 216 |  | 216 |  | 216 |  |  |  | 225.1
| Thermal Feedrate |  | MMBtu/hr |  | 3.89 |  | 3.89 |  | 3.89 |  | 3.89 |  |  |  | 4.7
| Heating Value |  | Btu/lb |  | 17990 |  | 17990 |  | 17990 |  | 17990
* | 733C4 | Trial Burn @ 80% Load |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  |  |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 |  |  |  | F2
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  |  |  | NG
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW |  |  |  | MF
| Feedstream Description |  |  |  | Liq waste |  | Liq waste |  | Liq waste |  | Liq waste |  |  |  | Natural gas
| Feed Rate |  | lb/hr |  | 194 |  | 194 |  | 194 |  | 194
| Thermal Feedrate |  | MMBtu/hr |  | 3.51 |  | 3.51 |  | 3.51 |  | 3.51 |  |  |  | 4.4
* | Heating Value |  | Btu/lb |  | 17990 |  | 17990 |  | 17990 |  | 17990
| 733C5 | Trial Burn @ 70% Load |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  |  |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 |  |  |  | F2
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  |  |  | NG
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW |  |  |  | MF
| Feedstream Description |  |  |  | Liq waste |  | Liq waste |  | Liq waste |  | Liq waste |  |  |  | Natural gas
* | Feed Rate |  | lb/hr |  | 172 |  | 172 |  | 172 |  | 172 |  |  |  | 192
| Thermal Feedrate |  | MMBtu/hr |  | 3.1 |  | 3.1 |  | 3.1 |  | 3.1 |  |  |  | 4
| Heating Value |  | Btu/lb |  | 17990 |  | 17990 |  | 17990 |  | 17990
| 733C6 | Trial Burn @ 40% Load |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  |  |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 |  |  |  | F2
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  |  |  | NG
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW |  |  |  | MF
| Feedstream Description |  |  |  | Liq waste |  | Liq waste |  | Liq waste |  | Liq waste |  |  |  | Natural gas
| Feed Rate |  | lb/hr |  | 85 |  | 85 |  | 85 |  | 85 |  |  |  | 119.9
| Thermal Feedrate |  | MMBtu/hr |  | 1.53 |  | 1.53 |  | 1.53 |  | 1.53 |  |  |  | 2.5
| Heating Value |  | Btu/lb |  | 17990 |  | 17990 |  | 17990 |  | 17990
BIF Feedrate Limits
| Arsenic |  | g/min | [7 empty] | 0.000833
| Antimony |  | g/min | [7 empty] | 0.906
| Barium |  | g/min | [7 empty] | 151
| Beryllium |  | g/min | [7 empty] | 0.00178
| Cadmium |  | g/min | [7 empty] | 0.000169
| Chromium |  | g/min | [7 empty] | 0.00183
| Lead |  | g/min | [7 empty] | 0.273
| Mercury |  | g/min | [7 empty] | 0.242
| Silver |  | g/min | [7 empty] | 9.06
| Thallium |  | g/min | [7 empty] | 1.51
| Chlorine |  | g/min | [7 empty] | 1.21