## list
source
cond
emiss
feed
process
df c3
df c4

## source
Source Description
Phase II ID No. | 735
EPA ID No. | IND000807107
Facility Name | Reilly Industries, Inc.
Facility Location
City | Indianapolis
State | IN
Unit ID Name/No. | Boiler 70K
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler, manufactured by Murray Iron Works Company, Model No. MCF4-64; thermal input capacity of 91.8 MMBtu/hr; steam production rate of 70000 lb/hr @ 300 psig
Capacity (MMBtu/hr) | 91.8
Soot Blowing | Yes -- 4 times/day, 5 minutes/event (Run 1 in Cond 1)
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics | NA
Hazardous Wastes | Liq
Haz Waste Description | Pyridine and pyrindine-derived organic chemical production waste
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 4.0016
Height (ft) | 75.9648
Gas Velocity (ft/sec) | 44.7
Gas Temperature (°F) | 615
Permitting Status | Adjusted Tier I metals except Cr (+6)
HWC Burn Status (Date if Terminated)

## cond
Cond Description
735C1
Report Name/Date | Revised Certification of Compliance Test Report for Boilers 70K, 30K, and 28K, August 21, 1996
Report Prepare | Spectrum Compliance Resources, Inc.
Testing Firm | Spectrum Compliance Resources, Inc., METCO Environmental, B3 Systems, Inc
Testing Dates | 1996-06-21
Cond Dates | 1996-06-01
Cond. Description | CoC; max waste feed
Content | PM, CO, Cr (+6), HCl/Cl2
735C2
Report Name/Date | Revised Certification of Compliance Test Report for Boilers 70K, 30K, and 28K, August 21, 1996
Report Prepare | Spectrum Compliance Resources, Inc.
Testing Firm | Spectrum Compliance Resources, Inc., METCO Environmental, B3 Systems, Inc
Testing Dates | June 21-22, 1996
Cond Dates | 1996-06-01
Cond. Description | CoC; min comb chamber temp
Content | CO
735C3
Report Name/Date | Trial Burn Report for Boiler 70K, February 3, 2000
Report Prepare | Compliance Strategies & Solutions, Inc.
Testing Firm | METCO Environmental (Stack sampling), B3 Systems, Inc (Feed spiking)
Testing Dates | October 21-23, 1999
Cond Dates | 1999-10-01
Cond Description | Trial burn; max waste feedrates
Content | PM, CO, HCl/Cl2, PCDD/PCDF emissions; metals/chlorine in feedstreams
735C4
Report Name/Date | Trial Burn Report for Boiler 70K, February 3, 2000
Report Prepare | Compliance Strategies & Solutions, Inc.
Testing Firm | METCO Environmental (Stack sampling), B3 Systems, Inc (Feed spiking)
Testing Dates | October 19-20, 1999
Cond Dates | 1999-10-01
Cond Description | Trial burn; min comb temp and DRE
Content | DRE, CO, PCDD/PCDF, organics
735C5
Report Name/Date | Trial Burn Report for Boiler 70K, February 3, 2000
Report Prepare | Compliance Strategies & Solutions, Inc.
Testing Firm | METCO Environmental (Stack sampling), B3 Systems, Inc (Feed spiking)
Testing Dates | 1999-11-04
Cond Dates | 1999-11-01
Cond Description | Trial burn; DRE test
Content | DRE, CO
735C6
Report Name/Date | Mini Burn Test Report for Boiler 70K, July 10, 2000
Report Prepare | Compliance Strategies & Solutions, Inc.
Testing Firm | METCO Environmental (Stack sampling), B3 Systems, Inc (Feed spiking)
Testing Dates | 2000-05-23
Cond Dates | 2000-05-01
Cond Description | Mini-burn, max waste feedrate
Content | Cr+6, CO
735C7
Report Name/Date | Trial Burn Retest Report for Boiler 70K, July 10, 2000
Report Prepare | Compliance Strategies & Solutions, Inc.
Testing Firm | METCO Environmental (Stack sampling), B3 Systems, Inc (Feed spiking)
Testing Dates | 2000-05-23
Cond Dates | 2000-05-01
Cond Description | Trial burn retest, min comb cham temp, min prod rate
Content | DRE

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
soot blow
1 | 735C1 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0804 |  | 0.0328 |  | 0.0327 |  | 0.0493
| CO (MHRA) | E1 | ppmv | y |  | 25.05 |  | 28.86 |  | 54.39 |  | 36.1
| CO (RA) | E1 | ppmv | y |  | 19.01 |  | 26.85 |  | 49.88 |  | 31.9133
| Chromium (Hex) |  | g/hr |  |  | 0.4536 |  | 0.4536 |  | 0.4536 |  | 0.4536
| HCl |  | g/hr |  |  | 3051 |  | 3320 |  | 3437 |  | 3265
| Cl2 |  | g/hr |  |  | 0.454 |  | 0.454 |  | 0.454 |  | 0.454
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 12874 |  | 12874 |  | 12874 |  | 12874
| O2 |  | % |  |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25
| Moisture |  | %
| Temperature |  | °F
| Chromium (Hex) | E1 | µg/dscm |  |  | 15.4935 |  | 15.4935 |  | 15.4935 |  | 15.4935
| HCl | E1 | ppmv | y |  | 71.8704 |  | 78.207 |  | 80.9631 |  | 77.0135
| Cl2 | E1 | ppmv | y |  | 0.022153 |  | 0.022153 |  | 0.022153 |  | 0.022153
| Total Chlorine | E1 | ppmv | y |  | 71.9147 |  | 78.2513 |  | 81.0074 |  | 77.0578
2 | 735C2 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| CO (RA) | E1 | ppmv | y |  | 2.51
| Sampling Train | CO | E1
| Stack Gas Flowrate |  | dscfm
| O2 |  | % |  |  | 8.3
| Moisture |  | %
| Temperature |  | °F
3 | 735C3 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
sootblow
| PM | E1 | gr/dscf | y |  | 0.0378 |  | 0.0282 |  | 0.0559 |  | 0.0375
| CO (MHRA) | E1 | ppmv | y |  | 9.88 |  | 21.46 |  | 20.81 |  | 17.3833
| HCl |  | lb/hr |  | nd | 0.03 | nd | 0.03 | nd | 0.04 | nd | 0.033333
| Cl2 |  | lb/hr |  | nd | 0.03 | nd | 0.03 | nd | 0.03 | nd | 0.03
| HC (RA) | E2 | ppmv |  | nd | 0.1 | nd | 0.1 |  | 0.3 |  | 0.16667
| HCl | E1 | ppmv | y | nd | 0.32204 | nd | 0.30817 | nd | 0.40881 |  | 0.34684
| Cl2 | E1 | ppmv | y | nd | 0.1656 | nd | 0.15847 | nd | 0.15767 |  | 0.16052
| Total Chlorine | E1 | ppmv | y | nd | 0.65324 |  | 0.62512 |  | 0.72415 |  | 0.66787
| HC (RA) | E1 | ppmv | y | nd | 0.08046 |  | 0.077778 |  | 0.23333 |  | 0.13109
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 13834 |  | 14036 |  | 14035 |  | 13968.3333
| O2 |  | % |  |  | 3.6 |  | 3 |  | 3 |  | 3.2
| Moisture |  | %
| Temperature |  | °F |  |  | 622 |  | 634 |  | 632 |  | 629.3333
| Sampling Train | HC | E2
| Stack Gas Flowrate |  | dscfm |  |  | 13383 |  | 13519 |  | 13588 |  | 13496.6667
| O2 |  | %
| Moisture |  | %
| Temperature |  | °F
4 | 735C4 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| CO (MHRA) | E1 | ppmv | y |  | 0.0006 |  | 0.0435 |  | 0 |  | 0.0147
| HC (RA) |  | ppmv |  | nd | 0.1 |  | 0.3 |  | 0.6 |  | 0.33333
| HC (RA) | E2 | ppmv | y | nd | 0.11111 |  | 0.30657 |  | 0.6087 |  | 0.34913
| POHC DRE | Benzene
| POHC Feedrate |  | g/hr |  |  | 3188.6266 |  | 3476.1636 |  | 3254.4893 |  | 3306.4265
Emissions Rate
| DRE |  | % |  |  | 99.9594 |  | 99.9616 |  | 99.9969
| Sampling Train | DRE | E1
| Stack Gas Flowrate |  | dscfm
| O2 |  | % |  |  | 8.4 |  | 7.3 |  | 7.2 |  | 7.6333
| Moisture |  | %
| Temperature |  | °F |  |  | 385 |  | 393 |  | 392 |  | 390
| Sampling Train | THC | E2
| Stack Gas Flowrate |  | dscfm |  |  | 5226 |  | 5603 |  | 5358 |  | 5395.6667
| O2 |  | %
| Moisture |  | %
| Temperature |  | °F
5 | 735C5 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| CO (MHRA) | E1 | ppmv | y |  | 0.264 |  | 0 |  | 0.001 |  | 0.088333
| POHC DRE | Benzene
| Feedrate |  | g/hr |  |  | 3942.7819 |  | 3548.9664 |  | 3905.3599
| Emissions Rate | E1 | lb/hr
| DRE | E1 | % |  |  | 99.147 |  | 99.337 |  | 99.465
| POHC DRE | Toluene
| Feedrate |  | g/hr |  |  | 29033.2123 |  | 27327.0413 |  | 28757.6503
| Emissions Rate | E1 | lb/hr
| DRE | E1 | % |  |  | 99.9874 |  | 99.9938 |  | 99.9946
| Sampling Train | DRE | E1
| Stack Gas Flowrate |  | dscfm |  |  | 6166 |  | 6321 |  | 6304 |  | 6263.6667
| O2 |  | % |  |  | 5.7 |  | 8.2 |  | 6 |  | 6.6333
| Moisture |  | %
| Temperature |  | °F |  |  | 420 |  | 426 |  | 430 |  | 425.3333
soot blow
6 | 735C6 | mini-burn |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| CO (RA) | E1 | ppmv | y |  | 22.86 |  |  |  | 13.22 |  | 18.04
| CO (MHRA) | E1 | ppmv | y |  | 28.78 |  |  |  | 20.84 |  | 24.81
| Chromium (Hex) |  | ug/dscm | n |  | 80.324 |  |  |  | 124.735 |  | 87.61
| Sampling Train | Cr+6 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 15621 |  | 15521 |  |  |  | 15571
| O2 |  | % |  |  | 2.1 |  | 2.8 |  |  |  | 2.45
| Moisture |  | % |  |  | 10.58 |  | 9.8 |  |  |  | 10.19
| Temperature |  | °F |  |  | 603 |  | 624 |  |  |  | 613.5
| Chromium (Hex) | E1 | ug/dscm | y |  | 59.4993 |  |  |  | 83.1567 |  | 66.1208
7 | 735C7 | trial burn retest |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| CO (RA) | E1 | ppmv | y |  | 0 |  | 0 |  | 0 |  | 0
| Benzene |  | g/s |  |  | 0.0148 |  | 0.00845 |  | 0.00974
| Toluene |  | g/s |  | nd | 0.00103 | nd | 0.000567 | nd | 0.000666
| POHC DRE | 1,2-dichlorobenzene
| Feedrate |  | g/hr |  |  | 20412 |  | 20399 |  | 20399
| Emissions Rate | E1 | g/s |  | nd | 5.06e-05 | nd | 5.12e-05 | nd | 5e-05
| DRE | E1 | % |  | > | 99.9991 | > | 99.9991 | > | 99.9991
| Sampling Train | DRE | E1
| Stack Gas Flowrate |  | dscfm |  |  | 12218 |  | 11747 |  | 11972 |  | 11979
| O2 |  | % |  |  | 6.8 |  | 6.9 |  | 6.8 |  | 6.8333
| Moisture |  | % |  |  | 12.37 |  | 11.37 |  | 12.48 |  | 12.0733
| Temperature |  | °F |  |  | 501 |  | 513 |  | 529 |  | 514.3333

## feed
Feedstreams
* | 735C1 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 |  | F3 |  | F3 |  | F3 |  | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | NG |  | NG |  | NG |  | NG |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | MF |  | MF |  | MF |  | MF |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | City Gas |  | City Gas |  | City Gas |  | City Gas |  | Spike Streams |  | Spike Streams |  | Spike Streams |  | Spike Streams |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 3741 |  | 3742 |  | 3747 |  | 3743.3333 | [7 empty] | 1344
| Density | g/ml |  | 0.962 |  | 0.963 |  | 0.963 |  | 0.96267
| Heat Content | Btu/lb |  | 14771 |  | 14788 |  | 14761 |  | 14773.3333 | [7 empty] | 21214
| Ash | g/hr |  | 2002.4 |  | 2172.6 |  | 2481.5 |  | 2218.8333 | [9 empty] | 2099.9 |  | 1714.7 |  | 2102.2 |  | 1972.2667
| Chlorine | g/hr |  | 729.67 |  | 1120.26 |  | 679.86 |  | 843.2633 | nd | 0.61 | nd | 0.61 | nd | 0.64 |  | 0.62 |  | 5186.27 |  | 4558.2 |  | 4555.56 |  | 4766.6767
| Antimony | g/hr | nd | 0.4073 | nd | 0.4074 | nd | 0.4249 |  | 0.4132 | nd | 0.0029 | nd | 0.0029 | nd | 0.0031 |  | 0.0029667 | nd | 0.194 | nd | 0.0178 | nd | 0.0174 |  | 0.0764
| Arsenic | g/hr | nd | 0.1188 | nd | 0.1188 | nd | 0.136 |  | 0.12453 |  | 0.0019 |  | 0.0019 |  | 0.002 |  | 0.0019333 | nd | 0.0314 | nd | 0.0279 | nd | 0.0181 |  | 0.0258
| Barium | g/hr | nd | 0.1697 | nd | 0.1697 | nd | 0.17 |  | 0.1698 | nd | 0.112 | nd | 0.1122 | nd | 0.1176 |  | 0.11393 | nd | 0.0113 | nd | 0.0073 | nd | 0.0074 |  | 0.0086667
| Beryllium | g/hr | nd | 0.0339 | nd | 0.0339 | nd | 0.034 |  | 0.033933 | nd | 0.0003 | nd | 0.0003 | nd | 0.0003 |  | 0.0003 | nd | 0.0016 | nd | 0.0015 | nd | 0.0015 |  | 0.0015333
| Cadmium | g/hr | nd | 0.0848 |  | 0.0849 | nd | 0.085 |  | 0.0849 | nd | 0.0016 | nd | 0.0016 | nd | 0.0017 |  | 0.0016333 | nd | 0.0373 | nd | 0.0327 | nd | 0.0147 |  | 0.028233
| Chromium | g/hr |  | 0.50908 |  | 0.54316 |  | 0.52689 |  | 0.52638 | nd | 0.00259 | nd | 0.0026 | nd | 0.00272 |  | 0.0026367 |  | 2.6299 |  | 2.3141 |  | 2.3324 |  | 2.425
| Lead | g/hr | nd | 0.1188 | nd | 0.1188 | nd | 0.119 |  | 0.11887 | nd | 0.0005 | nd | 0.0005 | nd | 0.0006 |  | 0.00053333 | nd | 0.015 | nd | 0.0124 | nd | 0.0254 |  | 0.0176
| Mercury | g/hr | nd | 0.0407 | nd | 0.0407 |  | 0.051 |  | 0.044133 | nd | 0.0006 | nd | 0.0006 | nd | 0.0006 |  | 0.0006 | nd | 0.0016 | nd | 0.0017 | nd | 0.0015 |  | 0.0016
| Silver | g/hr | nd | 0.4751 |  | 0.628 | nd | 0.4589 |  | 0.52067 | nd | 0.0016 | nd | 0.0016 | nd | 0.0016 |  | 0.0016 | nd | 0.0224 | nd | 0.0207 | nd | 0.0219 |  | 0.021667
| Thallium | g/hr | nd | 0.4073 | nd | 0.4074 | nd | 0.4249 |  | 0.4132 | nd | 0.0005 | nd | 0.0005 | nd | 0.0005 |  | 0.0005 | nd | 0.0194 | nd | 0.0178 | nd | 0.0179 |  | 0.018367
| Stack Gas Flowrate | dscfm |  | 12874 |  | 12874 |  | 12874 |  | 12874 |  | 12874 |  | 12874 |  | 12874 |  | 12874 |  | 12874 |  | 12874 |  | 12874 |  | 12874
| O2 | % |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25 |  | 2.25
| Thermal Feedrate | MMBtu/hr |  | 55.2583 |  | 55.3367 |  | 55.3095 |  | 55.3015 | [7 empty] | 28.5116 | [9 empty] | 83.7699 |  | 83.8483 |  | 83.8211 |  | 83.8131
| Estimated Firing Rate | MMBtu/hr | [31 empty] | 76.631
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 68.3953 |  | 74.2088 |  | 84.7598 | 0 | 75.788 | [9 empty] | 71.7256 |  | 58.5684 |  | 71.8042 | 0 | 67.3661 | 0 | 140.1209 | 0 | 132.7772 | 0 | 156.5639 | 0 | 143.154
| Chlorine | ug/dscm |  | 24923.1002 |  | 38264.3555 |  | 23221.7563 | 0 | 28803.0707 | 100 | 20.8356 | 100 | 20.8356 | 100 | 21.8603 | 100 | 21.1771 |  | 177145.7329 |  | 155692.9508 |  | 155602.7772 | 0 | 162813.8203 | 0.01031 | 202089.6687 | 0.010741 | 193978.1418 | 0.012223 | 178846.3937 | 0.011051 | 191638.0681
| Antimony | ug/dscm | 100 | 13.912 | 100 | 13.9154 | 100 | 14.5132 | 100 | 14.1135 | 100 | 0.099054 | 100 | 0.099054 | 100 | 0.10589 | 100 | 0.10133 | 100 | 6.6264 | 100 | 0.60799 | 100 | 0.59433 | 100 | 2.6096 | 100 | 20.6375 | 100 | 14.6225 | 100 | 15.2134 | 100 | 16.8244
| Arsenic | ug/dscm | 100 | 4.0578 | 100 | 4.0578 | 100 | 4.6453 | 100 | 4.2536 |  | 0.064898 |  | 0.064898 |  | 0.068313 | 0 | 0.066036 | 100 | 1.0725 | 100 | 0.95297 | 100 | 0.61824 | 100 | 0.88124 | 98.7508 | 5.1952 | 98.7214 | 5.0757 | 98.7188 | 5.3319 | 98.7303 | 5.2009
| Barium | ug/dscm | 100 | 5.7964 | 100 | 5.7964 | 100 | 5.8066 | 100 | 5.7998 | 100 | 3.8255 | 100 | 3.8324 | 100 | 4.0168 | 100 | 3.8916 | 100 | 0.38597 | 100 | 0.24934 | 100 | 0.25276 | 100 | 0.29602 | 100 | 10.0079 | 100 | 9.8781 | 100 | 10.0762 | 100 | 9.9874
| Beryllium | ug/dscm | 100 | 1.1579 | 100 | 1.1579 | 100 | 1.1613 | 100 | 1.159 | 100 | 0.010247 | 100 | 0.010247 | 100 | 0.010247 | 100 | 0.010247 | 100 | 0.054651 | 100 | 0.051235 | 100 | 0.051235 | 100 | 0.052374 | 100 | 1.2228 | 100 | 1.2194 | 100 | 1.2228 | 100 | 1.2217
| Cadmium | ug/dscm | 100 | 2.8965 |  | 2.8999 | 100 | 2.9033 | 66.6667 | 2.8999 | 100 | 0.054651 | 100 | 0.054651 | 100 | 0.058066 | 100 | 0.055789 | 100 | 1.274 | 100 | 1.1169 | 100 | 0.5021 | 100 | 0.96436 | 100 | 4.2252 | 28.7752 | 4.0715 | 100 | 3.4635 | 75.3413 | 3.92
| Chromium | ug/dscm |  | 17.3885 |  | 18.5525 |  | 17.9968 | 0 | 17.9793 | 100 | 0.088466 | 100 | 0.088807 | 100 | 0.092906 | 100 | 0.09006 |  | 89.8283 |  | 79.0437 |  | 79.6677 | 0 | 82.8466 | 0.082443 | 107.3052 | 0.090912 | 97.685 | 0.095037 | 97.7574 | 0.089242 | 100.9159
| Lead | ug/dscm | 100 | 4.0578 | 100 | 4.0578 | 100 | 4.0646 | 100 | 4.0601 | 100 | 0.017078 | 100 | 0.017078 | 100 | 0.020494 | 100 | 0.018217 | 100 | 0.51235 | 100 | 0.42354 | 100 | 0.86758 | 100 | 0.60116 | 100 | 4.5872 | 100 | 4.4984 | 100 | 4.9527 | 100 | 4.6795
| Mercury | ug/dscm | 100 | 1.3902 | 100 | 1.3902 |  | 1.742 | 61.4804 | 1.5074 | 100 | 0.020494 | 100 | 0.020494 | 100 | 0.020494 | 100 | 0.020494 | 100 | 0.054651 | 100 | 0.058066 | 100 | 0.051235 | 100 | 0.054651 | 100 | 1.4653 | 100 | 1.4687 | 3.9548 | 1.8137 | 63.3094 | 1.5826
| Silver | ug/dscm | 100 | 16.2278 |  | 21.4504 | 100 | 15.6745 | 59.7951 | 17.7842 | 100 | 0.054651 | 100 | 0.054651 | 100 | 0.054651 | 100 | 0.054651 | 100 | 0.76511 | 100 | 0.70704 | 100 | 0.74803 | 100 | 0.74006 | 100 | 17.0476 | 3.4292 | 22.2121 | 100 | 16.4772 | 61.5149 | 18.579
| Thallium | ug/dscm | 100 | 13.912 | 100 | 13.9154 | 100 | 14.5132 | 100 | 14.1135 | 100 | 0.017078 | 100 | 0.017078 | 100 | 0.017078 | 100 | 0.017078 | 100 | 0.66264 | 100 | 0.60799 | 100 | 0.6114 | 100 | 0.62734 | 100 | 14.5917 | 100 | 14.5405 | 100 | 15.1417 | 100 | 14.758
| SVM | ug/dscm | 100 | 6.9543 | 58.3211 | 6.9577 | 100 | 6.968 | 86.1116 | 6.96 | 100 | 0.071729 | 100 | 0.071729 | 100 | 0.07856 | 100 | 0.074006 | 100 | 1.7864 | 100 | 1.5405 | 100 | 1.3697 | 100 | 1.5655 | 100 | 8.8124 | 66.1618 | 8.5699 | 100 | 8.4162 | 88.7594 | 8.5995
| LVM | ug/dscm | 23.0741 | 22.6042 | 21.9441 | 23.7683 | 24.3941 | 23.8034 | 23.1391 | 23.392 | 60.334 | 0.16361 | 60.4167 | 0.16395 | 60.1594 | 0.17147 | 60.3012 | 0.16634 | 1.2393 | 90.9555 | 1.2545 | 80.0479 | 0.83333 | 80.3372 | 1.1144 | 83.7802 | 5.6643 | 113.7233 | 6.0771 | 103.9801 | 6.3073 | 104.3121 | 6.0059 | 107.3385
* | 735C2
nothing available
* | 735C3 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 |  | F3 |  | F3 |  | F3 |  | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | NG |  | NG |  | NG |  | NG |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | MF |  | MF |  | MF |  | MF |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | City Gas |  | City Gas |  | City Gas |  | City Gas |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 3694.8 |  | 3716.7 |  | 3689.2 |  | 3700.2 |  | 1043.4 |  | 1043.4 |  | 1043.4 |  | 1043.4 | [7 empty] | 37.1
| Density | g/ml |  | 0.9898 |  | 0.9898 |  | 0.9898 |  | 0.9898
| Heat Content | Btu/lb |  | 15381 |  | 15381 |  | 15381 |  | 15381 |  | 23350.3862 |  | 21214 |  | 21214 |  | 21214
| Ash | g/hr | nd | 1681.04 | nd | 1699.14 | nd | 1680.86 |  | 1686.6667 | [9 empty] | 3319.95 |  | 3203.25 |  | 3192.55 |  | 3238.6667
| Chlorine | g/hr | nd | 156.34 | nd | 141.03 | nd | 156.32 |  | 151 | [8 empty] | nd | 1.53 | nd | 1.53 | nd | 1.52 |  | 1.56
| Antimony | g/hr | nd | 0.34 | nd | 0.34 | nd | 0.34 |  | 0.34 | [8 empty] | nd | 0.001 | nd | 0.001 | nd | 0.004 |  | 0.001
| Arsenic | g/hr | nd | 0.34 | nd | 0.34 | nd | 0.34 |  | 0.34 | [8 empty] | nd | 0.002 | nd | 0.002 | nd | 0.002 |  | 0.002
| Barium | g/hr | nd | 0.1 | nd | 0.11 | nd | 0.1 |  | 0.1 | [9 empty] | 0.006 |  | 0.007 |  | 0.007 |  | 0.006
| Beryllium | g/hr | nd | 0.17 | nd | 0.17 | nd | 0.17 |  | 0.17 | [8 empty] | nd | 0.002 | nd | 0.002 | nd | 0.0002 |  | 0.002
| Cadmium | g/hr | nd | 0.17 | nd | 0.17 | nd | 0.17 |  | 0.17 | [9 empty] | 0.003 |  | 0.003 |  | 0.002 |  | 0.0027
| Chromium | g/hr |  | 2.02 |  | 1.39 |  | 1.51 |  | 1.64 | [9 empty] | 0.005 |  | 0.005 |  | 0.006 |  | 0.0053
| Lead | g/hr | nd | 0.05 | nd | 0.04 | nd | 0.05 |  | 0.05 | [9 empty] | 0.003 |  | 0.003 |  | 0.002 |  | 0.0027
| Mercury | g/hr |  | 0.08 | nd | 0.07 | nd | 0.07 |  | 0.061667 | [8 empty] | nd | 0.0007 | nd | 0.0001 | nd | 0.0001 |  | 0.0007
| Silver | g/hr | nd | 0.17 | nd | 0.17 | nd | 0.17 |  | 0.17 | [8 empty] | nd | 0.002 | nd | 0.002 | nd | 0.002 |  | 0.002
| Thallium | g/hr | nd | 0.17 | nd | 0.17 | nd | 0.17 |  | 0.17 | [8 empty] | nd | 0.002 | nd | 0.002 | nd | 0.002 |  | 0.002
| Stack Gas Flowrate | dscfm |  | 13834 |  | 14036 |  | 14035 |  | 13968.3333 |  | 13834 |  | 14036 |  | 14035 |  | 13968.3333 |  | 13834 |  | 14036 |  | 14035 |  | 13968.3333
| O2 | % |  | 3.6 |  | 3 |  | 3 |  | 3.2 |  | 3.6 |  | 3 |  | 3 |  | 3.2 |  | 3.6 |  | 3 |  | 3 |  | 3.2
| Thermal Feedrate | MMBtu/hr |  | 56.8297 |  | 57.1666 |  | 56.7436 |  | 56.9128 | [7 empty] | 22.1347 | [9 empty] | 78.9644 |  | 79.3013 |  | 78.8783 |  | 79.0475
| Estimated Firing Rate | MMBtu/hr | [31 empty] | 78.9322
Feedrate MTEC Calculations
| Ash | mg/dscm | 100 | 57.58 | 100 | 55.4503 | 100 | 54.8576 | 100 | 55.9626 | [9 empty] | 113.7169 |  | 104.5359 |  | 104.1941 | 0 | 107.4823 | 33.6141 | 171.2968 | 34.6594 | 159.9861 | 34.4904 | 159.0517 | 34.2394 | 163.4449
| Chlorine | ug/dscm | 100 | 5355.0489 | 100 | 4602.4173 | 100 | 5101.7594 | 100 | 5019.7418 | [8 empty] | 100 | 52.4065 | 100 | 49.9305 | 100 | 49.6077 | 100 | 50.6482 | 100 | 5407.4553 | 100 | 4652.3478 | 100 | 5151.3671 | 100 | 5070.3901
| Antimony | ug/dscm | 100 | 11.6459 | 100 | 11.0957 | 100 | 11.0965 | 100 | 11.2793 | [8 empty] | 100 | 0.034253 | 100 | 0.032634 | 100 | 0.13055 | 100 | 0.065811 | 100 | 11.6801 | 100 | 11.1283 | 100 | 11.227 | 100 | 11.3451
| Arsenic | ug/dscm | 100 | 11.6459 | 100 | 11.0957 | 100 | 11.0965 | 100 | 11.2793 | [8 empty] | 100 | 0.068505 | 100 | 0.065269 | 100 | 0.065273 | 100 | 0.066349 | 100 | 11.7144 | 100 | 11.1609 | 100 | 11.1617 | 100 | 11.3457
| Barium | ug/dscm | 100 | 3.4253 | 100 | 3.5898 | 100 | 3.2637 | 100 | 3.4262 | [9 empty] | 0.20552 |  | 0.22844 |  | 0.22846 | 0 | 0.2208 | 94.3396 | 3.6308 | 94.0171 | 3.8182 | 93.4579 | 3.4921 | 93.9457 | 3.647
| Beryllium | ug/dscm | 100 | 5.8229 | 100 | 5.5478 | 100 | 5.5482 | 100 | 5.6397 | [8 empty] | 100 | 0.068505 | 100 | 0.065269 | 100 | 0.0065273 | 100 | 0.046767 | 100 | 5.8914 | 100 | 5.6131 | 100 | 5.5548 | 100 | 5.6864
| Cadmium | ug/dscm | 100 | 5.8229 | 100 | 5.5478 | 100 | 5.5482 | 100 | 5.6397 | [9 empty] | 0.10276 |  | 0.097903 |  | 0.065273 | 0 | 0.088645 | 98.2659 | 5.9257 | 98.2659 | 5.6457 | 98.8372 | 5.6135 | 98.4525 | 5.7283
| Chromium | ug/dscm |  | 69.1902 |  | 45.3617 |  | 49.2813 | 0 | 54.6111 | [9 empty] | 0.17126 |  | 0.16317 |  | 0.19582 | 0 | 0.17675 | 0 | 69.3615 | 0 | 45.5249 | 0 | 49.4771 | 0 | 54.7878
| Lead | ug/dscm | 100 | 1.7126 | 100 | 1.3054 | 100 | 1.6318 | 100 | 1.5499 | [9 empty] | 0.10276 |  | 0.097903 |  | 0.065273 | 0 | 0.088645 | 94.3396 | 1.8154 | 93.0233 | 1.4033 | 96.1538 | 1.6971 | 94.5902 | 1.6386
| Mercury | ug/dscm |  | 2.7402 | 100 | 2.2844 | 100 | 2.2846 | 62.51 | 2.4364 | [8 empty] | 100 | 0.023977 | 100 | 0.0032634 | 100 | 0.0032637 | 100 | 0.010168 | 0.86741 | 2.7642 | 100 | 2.2877 | 100 | 2.2878 | 62.6658 | 2.4466
| Silver | ug/dscm | 100 | 5.8229 | 100 | 5.5478 | 100 | 5.5482 | 100 | 5.6397 | [8 empty] | 100 | 0.068505 | 100 | 0.065269 | 100 | 0.065273 | 100 | 0.066349 | 100 | 5.8914 | 100 | 5.6131 | 100 | 5.6135 | 100 | 5.706
| Thallium | ug/dscm | 100 | 5.8229 | 100 | 5.5478 | 100 | 5.5482 | 100 | 5.6397 | [8 empty] | 100 | 0.068505 | 100 | 0.065269 | 100 | 0.065273 | 100 | 0.066349 | 100 | 5.8914 | 100 | 5.6131 | 100 | 5.6135 | 100 | 5.706
| SVM | ug/dscm | 100 | 7.5356 | 100 | 6.8532 | 100 | 7.1801 | 100 | 7.1896 | [8 empty] | 0 | 0.20552 | 0 | 0.19581 | 0 | 0.13055 | 0 | 0.17729 | 97.3451 | 7.7411 | 97.2222 | 7.049 | 98.2143 | 7.3106 | 97.5934 | 7.3669
| LVM | ug/dscm | 20.1581 | 86.659 | 26.8421 | 62.0052 | 25.2475 | 65.926 | 23.653 | 71.5301 | [8 empty] | 44.4444 | 0.30827 | 44.4444 | 0.29371 | 26.8293 | 0.26762 | 39.0234 | 0.28987 | 20.2442 | 86.9673 | 26.9251 | 62.2989 | 25.2539 | 66.1936 | 23.715 | 71.8199
* | 735C4 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 |  | F3 |  | F3 |  | F3 |  | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | NG |  | NG |  | NG |  | NG |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | MF |  | MF |  | MF |  | MF |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 580.5 |  | 578.7 |  | 594.8 |  | 584.6667 |  | 672.7 |  | 672.7 |  | 672.7 |  | 672.7
| Density | g/ml |  | 0.962 |  | 0.963 |  | 0.963 |  | 0.96267
| Heat Content | Btu/lb |  | 14771 |  | 14788 |  | 14761 |  | 14773.3333 |  | 21214 |  | 21214 |  | 21214 |  | 21214
| O2 | % | [7 empty] | 7.04
| Thermal Feedrate | MMBtu/hr |  | 8.5746 |  | 8.5578 |  | 8.7798 |  | 8.6375 |  | 14.2707 |  | 14.2707 |  | 14.2707 |  | 14.2707 | [9 empty] | 17.212 |  | 22.8285 |  | 23.0505 |  | 22.9081
* | 735C5 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 |  | F3 |  | F3 |  | F3 |  | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | NG |  | NG |  | NG |  | NG |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | MF |  | MF |  | MF |  | MF |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Spike |  | Spike |  | Spike |  | Spike | [7 empty] | Total
| Feed Rate | lb/hr |  | 790.2 |  | 782.4 |  | 782.7 |  | 785.1 |  | 882.6 |  | 882.6 |  | 882.6 |  | 882.6
| Density | g/ml |  | 0.9898 |  | 0.9898 |  | 0.9898 |  | 0.9898
| Heat Content | Btu/lb |  | 15000 |  | 15000 |  | 15000 |  | 15000 |  | 21214 |  | 21214 |  | 21214 |  | 21214
| O2 | % |  | 5.7 |  | 8.2 |  | 6 |  | 6.6333
| Stack Gas Flowrate | dscfm |  | 6166 |  | 6321 |  | 6304 |  | 6263.6667
| Thermal Feedrate | MMBtu/hr |  | 11.853 |  | 11.736 |  | 11.7405 |  | 11.7765 |  | 18.7235 |  | 18.7235 |  | 18.7235 |  | 18.7235 | [15 empty] | 30.5
| Estimated Firing Rate | MMBtu/hr | [31 empty] | 28.5676
* | 735C6 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 |  | F3 |  | F3 |  | F3 |  | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | NG |  | NG |  | NG |  | NG |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | MF |  | MF |  | MF |  | MF |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste |  | Waste |  | Waste |  | Waste |  | City gas |  | City gas |  | City gas |  | City gas |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 3522.8 |  | 3522.8 |  | 3522.8 |  | 3522.8 |  | 1103.3 |  | 1103.3 |  | 1103.3 |  | 1103.3
| Chromium | g/hr |  | 1.7 |  | 1.7 |  | 1.7 |  | 1.7 | [9 empty] | 7.72 |  | 7.72 |  | 7.72 |  | 7.72
| Stack Gas Flowrate | dscfm |  | 15621 |  | 15521 |  |  |  | 15571 |  | 0 |  | 0 |  | 15621 |  | 15521 |  | 15621 |  | 15521 |  |  |  | 15571
| O2 | % |  | 2.1 |  | 2.8 |  |  |  | 2.45 |  | 0 |  | 0 |  | 2.1 |  | 2.8 |  | 2.1 |  | 2.8 |  |  |  | 2.45
| Chromium | ug/dscm |  | 47.4754 |  | 49.619 |  |  |  | 48.5265 | [9 empty] | 215.5942 |  | 225.3287 |  |  |  | 220.3673 |  | 263.0696 |  | 274.9477 |  | 0 |  | 269.0087
* | 735C7 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | NG |  | NG |  | NG |  | NG
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | MF |  | MF |  | MF |  | MF
| Feedstream Description |  |  | Waste |  | Waste |  | Waste |  | Waste |  | City gas |  | City gas |  | City gas |  | City gas
| Feedrate | lb/hr |  | 1538.8 |  | 1538.8 |  | 1538.8 |  | 1538.8 |  | 1114.4 |  | 1114.4 |  | 1114.4 |  | 1114.4
BIF Feedrate Limits
| Antimony | g/hr | [7 empty] | 1620
| Arsenic | g/hr | [7 empty] | 12.42
| Barium | g/hr | [7 empty] | 270037
| Beryllium | g/hr | [7 empty] | 22.68
| Cadmium | g/hr | [7 empty] | 30.24
| Chromium | g/hr | [7 empty] | 4.48
| Lead | g/hr | [7 empty] | 486
| Mercury | g/hr | [7 empty] | 1620
| Silver | g/hr | [7 empty] | 16202
| Thallium | g/hr | [7 empty] | 2700
| Chlorine | g/hr | [7 empty] | 40000

## process
Process Information
| Units | CondAvg
735C1
Chamber Temp | °F | 1680.77
Steam Production Rate | klb/hr | 68.12
735C2
Chamber Temp | °F | 1065.8
Steam Production Rate | klb/hr | 15.9
735C3
Chamber Temp | °F | 1794.4
Steam Production Rate | klb/hr | 64.8
735C4
Chamber Temp | °F | 1272.5
Steam Production Rate | klb/hr | 20.48
735C5
Chamber Temp | °F | 1427
Steam Production Rate | klb/hr | 26.99
735C6
Chamber Temp | °F | 1736
Steam Production Rate | klb/hr | 65.86
735C7
Chamber Temp | °F | 1537.1
Steam Production Rate | klb/hr | 32.43

## df c3
PCDD/PCDF
N
Facility Name and ID: |  | Reilly Industries, Inc.
Condition ID: |  | 735C3
Condition/Test Date: |  | October 21-23, 1999
|  | I-TEF |  | Run 1 |  |  |  |  | Run 2 |  |  |  |  | Run 3
|  | Wght Fact |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ
|  |  |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND
Stack Gas Concentration (ng/dscm @ 7% O2)
| 2,3,7,8-TCDD | 1 | nd | 0.00171 | 0.00171 | 0.000855 | 0.000855 | nd | 0.0021 | 0.0021 | 0.00105 | 0.00105 | nd | 0.00227 | 0.00227 | 0.001135 | 0.001135
| TCDD Total | 0
| 1,2,3,7,8-PCDD | 0.5 | nd | 0.00248 | 0.00124 | 0.00124 | 0.00062 | nd | 0.00202 | 0.00101 | 0.00101 | 0.000505 | nd | 0.001484 | 0.000742 | 0.000742 | 0.000371
| PCDD Total | 0
| 1,2,3,4,7,8-HxCDD | 0.1 | nd | 0.00295 | 0.000295 | 0.001475 | 0.0001475 | nd | 0.00307 | 0.000307 | 0.001535 | 0.0001535 | nd | 0.00225 | 0.000225 | 0.001125 | 0.0001125
| 1,2,3,6,7,8-HxCDD | 0.1 | nd | 0.00284 | 0.000284 | 0.00142 | 0.000142 | nd | 0.00297 | 0.000297 | 0.001485 | 0.0001485 | nd | 0.00216 | 0.000216 | 0.00108 | 0.000108
| 1,2,3,7,8,9-HxCDD | 0.1 | nd | 0.0027 | 0.00027 | 0.00135 | 0.000135 | nd | 0.00278 | 0.000278 | 0.00139 | 0.000139 | nd | 0.00205 | 0.000205 | 0.001025 | 0.0001025
| HxCDD Total | 0
| 1,2,3,4,6,7,8-HpCDD | 0.01 | nd | 0.00301 | 3.01e-05 | 0.001505 | 1.505e-05 | nd | 0.00342 | 3.42e-05 | 0.00171 | 1.71e-05 | nd | 0.00293 | 2.93e-05 | 0.001465 | 1.465e-05
| HpCDD Total | 0
| OCDD | 0.001 | nd | 0.00815 | 8.15e-06 | 0.004075 | 4.075e-06 | nd | 0.0122 | 1.22e-05 | 0.0061 | 6.1e-06 | nd | 0.0105 | 1.05e-05 | 0.00525 | 5.25e-06
| 2,3,7,8-TCDF | 0.1 | nd | 0.00272 | 0.000272 | 0.00136 | 0.000136 | nd | 0.00258 | 0.000258 | 0.00129 | 0.000129 | nd | 0.00145 | 0.000145 | 0.000725 | 7.25e-05
| TCDF Total | 0
| 1,2,3,7,8-PCDF | 0.05 | nd | 0.00318 | 0.000159 | 0.00159 | 7.95e-05 | nd | 0.00266 | 0.000133 | 0.00133 | 6.65e-05 | nd | 0.00236 | 0.000118 | 0.00118 | 5.9e-05
| 2,3,4,7,8-PCDF | 0.5 | nd | 0.00328 | 0.00164 | 0.00164 | 0.00082 | nd | 0.00272 | 0.00136 | 0.00136 | 0.00068 | nd | 0.00244 | 0.00122 | 0.00122 | 0.00061
| PCDF Total | 0
| 1,2,3,4,7,8-HxCDF | 0.1 | nd | 0.00121 | 0.000121 | 0.000605 | 6.05e-05 | nd | 0.00185 | 0.000185 | 0.000925 | 9.25e-05 | nd | 0.0015 | 0.00015 | 0.00075 | 7.5e-05
| 1,2,3,6,7,8-HxCDF | 0.1 | nd | 0.000962 | 9.62e-05 | 0.000481 | 4.81e-05 | nd | 0.00146 | 0.000146 | 0.00073 | 7.3e-05 | nd | 0.00118 | 0.000118 | 0.00059 | 5.9e-05
| 2,3,4,6,7,8-HxCDF | 0.1 | nd | 0.000962 | 9.62e-05 | 0.000481 | 4.81e-05 | nd | 0.00142 | 0.000142 | 0.00071 | 7.1e-05 | nd | 0.00116 | 0.000116 | 0.00058 | 5.8e-05
| 1,2,3,7,8,9-HxCDF | 0.1 | nd | 0.00144 | 0.000144 | 0.00072 | 7.2e-05 | nd | 0.00216 | 0.000216 | 0.00108 | 0.000108 | nd | 0.00177 | 0.000177 | 0.000885 | 8.85e-05
| HxCDF Total | 0
| 1,2,3,4,6,7,8-HpCDF | 0.01 | nd | 0.00159 | 1.59e-05 | 0.000795 | 7.95e-06 | nd | 0.00338 | 3.38e-05 | 0.00169 | 1.69e-05 | nd | 0.00173 | 1.73e-05 | 0.000865 | 8.65e-06
| 1,2,3,4,7,8,9-HpCDF | 0.01 | nd | 0.00174 | 1.74e-05 | 0.00087 | 8.7e-06 | nd | 0.00157 | 1.57e-05 | 0.000785 | 7.85e-06 | nd | 0.00192 | 1.92e-05 | 0.00096 | 9.6e-06
| HpCDF Total | 0
| OCDF | 0.001 | nd | 0.00836 | 8.36e-06 | 0.00418 | 4.18e-06 | nd | 0.012 | 1.2e-05 | 0.006 | 6e-06 | nd | 0.00995 | 9.95e-06 | 0.004975 | 4.975e-06
| PCDD/PCDF (ng/dscm @ 7% O2) |  | 100 |  | 0.0064073 |  | 0.0032037 | 100 |  | 0.0065399 |  | 0.00327 | 100 |  | 0.0057882 |  | 0.0028941
| TEQ Cond Avg | 0.0031226

## df c4
PCDD/PCDF
N
Facility Name and ID: |  | Reilly Ind.
Condition ID: |  | 735C4
Condition/Test Date: |  | October 19-20, 1999
|  | I-TEF |  | Run 1 |  |  |  |  | Run 2 |  |  |  |  | Run 3
|  | Wght Fact |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ
|  |  |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND
Stack Gas Concentration (ng/dscm @ 7% O2)
| 2,3,7,8-TCDD | 1 | nd | 0.00221 | 0.00221 | 0.001105 | 0.001105 | nd | 0.00151 | 0.00151 | 0.000755 | 0.000755 | nd | 0.00287 | 0.00287 | 0.001435 | 0.001435
| TCDD Total | 0
| 1,2,3,7,8-PCDD | 0.5 | nd | 0.00374 | 0.00187 | 0.00187 | 0.000935 | nd | 0.0026 | 0.0013 | 0.0013 | 0.00065 | nd | 0.00316 | 0.00158 | 0.00158 | 0.00079
| PCDD Total | 0
| 1,2,3,4,7,8-HxCDD | 0.1 | nd | 0.00371 | 0.000371 | 0.001855 | 0.0001855 | nd | 0.00209 | 0.000209 | 0.001045 | 0.0001045 | nd | 0.00325 | 0.000325 | 0.001625 | 0.0001625
| 1,2,3,6,7,8-HxCDD | 0.1 | nd | 0.00362 | 0.000362 | 0.00181 | 0.000181 | nd | 0.00204 | 0.000204 | 0.00102 | 0.000102 | nd | 0.00313 | 0.000313 | 0.001565 | 0.0001565
| 1,2,3,7,8,9-HxCDD | 0.1 | nd | 0.00339 | 0.000339 | 0.001695 | 0.0001695 | nd | 0.00193 | 0.000193 | 0.000965 | 9.65e-05 | nd | 0.00293 | 0.000293 | 0.001465 | 0.0001465
| HxCDD Total | 0
| 1,2,3,4,6,7,8-HpCDD | 0.01 | nd | 0.00912 | 9.12e-05 | 0.00456 | 4.56e-05 | nd | 0.00288 | 2.88e-05 | 0.00144 | 1.44e-05 | nd | 0.00439 | 4.39e-05 | 0.002195 | 2.195e-05
| HpCDD Total | 0
| OCDD | 0.001 |  | 0.0401 | 4.01e-05 | 0.0401 | 4.01e-05 |  | 0.0243 | 2.43e-05 | 0.0243 | 2.43e-05 |  | 0.0299 | 2.99e-05 | 0.0299 | 2.99e-05
| 2,3,7,8-TCDF | 0.1 | nd | 0.00218 | 0.000218 | 0.00109 | 0.000109 | nd | 0.00134 | 0.000134 | 0.00067 | 6.7e-05 | nd | 0.00272 | 0.000272 | 0.00136 | 0.000136
| TCDF Total | 0
| 1,2,3,7,8-PCDF | 0.05 | nd | 0.00342 | 0.000171 | 0.00171 | 8.55e-05 | nd | 0.0021 | 0.000105 | 0.00105 | 5.25e-05 | nd | 0.00246 | 0.000123 | 0.00123 | 6.15e-05
| 2,3,4,7,8-PCDF | 0.5 | nd | 0.00352 | 0.00176 | 0.00176 | 0.00088 | nd | 0.00218 | 0.00109 | 0.00109 | 0.000545 | nd | 0.00254 | 0.00127 | 0.00127 | 0.000635
| PCDF Total | 0
| 1,2,3,4,7,8-HxCDF | 0.1 | nd | 0.00277 | 0.000277 | 0.001385 | 0.0001385 | nd | 0.00134 | 0.000134 | 0.00067 | 6.7e-05 | nd | 0.00179 | 0.000179 | 0.000895 | 8.95e-05
| 1,2,3,6,7,8-HxCDF | 0.1 | nd | 0.00221 | 0.000221 | 0.001105 | 0.0001105 | nd | 0.00109 | 0.000109 | 0.000545 | 5.45e-05 | nd | 0.00144 | 0.000144 | 0.00072 | 7.2e-05
| 2,3,4,6,7,8-HxCDF | 0.1 | nd | 0.00215 | 0.000215 | 0.001075 | 0.0001075 | nd | 0.00103 | 0.000103 | 0.000515 | 5.15e-05 | nd | 0.00141 | 0.000141 | 0.000705 | 7.05e-05
| 1,2,3,7,8,9-HxCDF | 0.1 | nd | 0.00326 | 0.000326 | 0.00163 | 0.000163 | nd | 0.00156 | 0.000156 | 0.00078 | 7.8e-05 | nd | 0.00211 | 0.000211 | 0.001055 | 0.0001055
| HxCDF Total | 0
| 1,2,3,4,6,7,8-HpCDF | 0.01 | nd | 0.00313 | 3.13e-05 | 0.001565 | 1.565e-05 | nd | 0.00215 | 2.15e-05 | 0.001075 | 1.075e-05 | nd | 0.00196 | 1.96e-05 | 0.00098 | 9.8e-06
| 1,2,3,4,7,8,9-HpCDF | 0.01 | nd | 0.00349 | 3.49e-05 | 0.001745 | 1.745e-05 | nd | 0.00237 | 2.37e-05 | 0.001185 | 1.185e-05 | nd | 0.00217 | 2.17e-05 | 0.001085 | 1.085e-05
| HpCDF Total | 0
| OCDF | 0.001 | nd | 0.00879 | 8.79e-06 | 0.004395 | 4.395e-06 | nd | 0.00625 | 6.25e-06 | 0.003125 | 3.125e-06 | nd | 0.0123 | 1.23e-05 | 0.00615 | 6.15e-06
| PCDD/PCDF (ng/dscm @ 7% O2) |  | 99.5308 |  | 0.0085463 |  | 0.0042932 | 99.5459 |  | 0.0053515 |  | 0.0026879 | 99.619 |  | 0.0078484 |  | 0.0039391
| TEQ Cond Avg | 0.0036401