## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 741
EPA ID No. | KYD006390017
Facility Name | Rohm and Haas Company
Facility Location
City | Louisville
State | KY
Unit ID Name/No. | Unit No. 100
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler. ABB Combustion type 35-A-14, 180000 lb/hr of steam @ 400 psig, frontwall burner, economizer, FGR, 248 MMBtu/hr
Capacity (MMBtu/hr) | 248
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics
Hazardous Wastes | Liq
Haz Waste Descript | Liquid wastes
Supplemental Fuel | Natural gas, oil
No. 2 fuel oil
Stack Characteristics
Diameter (ft) | 6.5
Height (ft) | 212
Gas Velocity* (ft/sec) | 29.3333
Gas Temperature* (°F) | 434
Permitting Status | Adjusted Tier I metals and chlorine
HWC Burn Status (Date if Terminated)
* At sample location on stack which has a diameter of 7.83 feet.
* At sample location on stack which has a diameter of 7.83 feet.

## cond
Cond Description
741C1
Report Name/Date | Certification of Compliance Boiler No. 100, Nov. 19, 1999
Report Preparer | Focus Environmental, Inc.
Testing Firm | TRC Environmental Corporation
Testing Dates | August 26-27, 1999
Cond Dates | 1999-08-01
Condition Descr | CoC; max waste feed rate, ash spiking (TiO2)
Content | PM, CO in stack gas; metals, chlorine and ash in feedstreams

## emiss
Stack Gas Emissions
| Comments | Units | 7% O2 |  |  | Soot | Soot Blow
[6 empty] | Blowing | Corrected
741C1 |  |  |  | R1 | R2 | R3 | Cond Avg
PM | E1 | gr/dscf | y | 0.028 | 0.032 | 0.044 | 0.0312
CO (RA) | E1 | ppmv | y | 16.79 | 11.82 | 6.9 | 11.8367
CO (MHRA) | E1 | ppmv | y | 28.05 | 24.03 | 7.96 | 20.0133
Sampling Train | PM | E1
Gas Flowrate |  | dscfm |  | 41041 | 41680 | 43752 | 42157.6667
Oxygen |  | % |  | 4 | 5.3 | 5.5 | 4.9333
Moisture |  | % |  | 14.3 | 14.2 | 15.3 | 14.6
Gas Temperature |  | °F |  | 435.3 | 437.3 | 429.8 | 434.1333
PM |  | g/hr |  | 5339 | 5796 | 8387 | 6507.3333 | Uncorrected
[7 empty] | 5857 | Corrected Avg

## feed
Feedstreams
741C1 |  |  | Cond Avg | Cond Avg | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
Feedstream Number |  |  | F1 | F2 | F3 |  | F4 |  | F4 |  | F4 |  | F4
Feed Class |  |  | Liq HW | Spike | NG |  | Total |  | Total |  | Total |  | Total
Feed Class 2 |  |  | HW | Spike | MF |  | Total |  | Total |  | Total |  | Total
Feedstream Description |  |  | Haz waste | Spiking TiO2 | Natural Gas |  | Total |  | Total |  | Total |  | Total
Feed Rate | lb/hr |  | 12393
Main gun | lb/hr |  | 9302 | 31
Side gun | lb/hr |  | 3091
Feed Rate | dscfh |  |  |  | 50400
Heating Value | Btu/scf |  |  |  | 1022
Main gun | Btu/lb |  | 11000 | 8393
Side gun | Btu/lb |  | 17000
Ash | g/hr | nd | 607 | 5803 |  | nd | 6320 | nd | 6730 | nd | 6170
Chlorine | g/hr |  | 1691 |  |  |  | 2510 |  | 1280 |  | 1270
Antimony | g/hr | nd | 17.1 |  |  | nd | 17 | nd | 17 | nd | 18
Arsenic | g/hr | nd | 14.1 |  |  | nd | 14 | nd | 14 | nd | 14
Barium | g/hr | nd | 1.1 |  |  | nd | 1.1 | nd | 1.1 | nd | 1.1
Beryllium | g/hr | nd | 0.56 |  |  | nd | 0.56 | nd | 0.57 | nd | 0.56
Cadmium | g/hr | nd | 1.1 |  |  | nd | 1.1 | nd | 1.1 | nd | 1.1
Chromium | g/hr | nd | 39.4 |  |  | nd | 62 | nd | 28 | nd | 28
Chromium (Hex) | g/hr | nd | 1.97 |  |  |  | 1.8 |  | 1.8 | nd | 2.3
Lead | g/hr | nd | 56.2 |  |  | nd | 56 | nd | 57 | nd | 56
Mercury | g/hr | nd | 0.27 |  |  | nd | 0.22 | nd | 0.39 | nd | 0.27
Silver | g/hr | nd | 2.8 |  |  | nd | 2.8 | nd | 2.8 | nd | 2.8
Thallium | g/hr | nd | 112 |  |  | nd | 111 | nd | 113 | nd | 113
Stack Gas Flowrate | dscfm |  | 42158 | 42158 |  |  | 41041 |  | 41680 |  | 43752 |  | 42157.6667
Oxygen | % |  | 4.9 | 4.9 |  |  | 4 |  | 5.3 |  | 5.5 |  | 4.9333
Thermal Feedrate | MMBtu/hr |  | 154.869 |  | 51.5088 | [7 empty] | 206.3778
Estimated Firing Rate | MMBtu/hr | [11 empty] | 215.4742
Feedrate MTEC Calculations
Ash | mg/dscm | 100 | 7.3735 | 70.4915 |  | 100 | 74.6862 | 100 | 84.7965 | 100 | 75.0146 | 100 | 78.1658
Chlorine | ug/dscm |  | 20541.3074 |  |  |  | 29661.7804 |  | 16127.7193 |  | 15440.6103 |  | 20410.0367
Antimony | ug/dscm | 100 | 207.7211 |  |  | 100 | 200.8965 | 100 | 214.1963 | 100 | 218.8433 | 100 | 211.312
Arsenic | ug/dscm | 100 | 171.2788 |  |  | 100 | 165.4442 | 100 | 176.3969 | 100 | 170.2115 | 100 | 170.6842
Barium | ug/dscm | 100 | 13.3622 |  |  | 100 | 12.9992 | 100 | 13.8598 | 100 | 13.3738 | 100 | 13.4109
Beryllium | ug/dscm | 100 | 6.8026 |  |  | 100 | 6.6178 | 100 | 7.1819 | 100 | 6.8085 | 100 | 6.8694
Cadmium | ug/dscm | 100 | 13.3622 |  |  | 100 | 12.9992 | 100 | 13.8598 | 100 | 13.3738 | 100 | 13.4109
Chromium | ug/dscm | 100 | 478.6088 |  |  | 100 | 732.6814 | 100 | 352.7939 | 100 | 340.4229 | 100 | 475.2994
Chromium (Hex) | ug/dscm | 100 | 23.9304 |  |  |  | 21.2714 |  | 22.6796 | 100 | 27.9633 | 38.8842 | 23.9714
Lead | ug/dscm | 100 | 682.6857 |  |  | 100 | 661.7768 | 100 | 718.1875 | 100 | 680.8458 | 100 | 686.9367
Mercury | ug/dscm | 100 | 3.2798 |  |  | 100 | 2.5998 | 100 | 4.9139 | 100 | 3.2826 | 100 | 3.5988
Silver | ug/dscm | 100 | 34.0128 |  |  | 100 | 33.0888 | 100 | 35.2794 | 100 | 34.0423 | 100 | 34.1368
Thallium | ug/dscm | 100 | 1360.5124 |  |  | 100 | 1311.7361 | 100 | 1423.7752 | 100 | 1373.8496 | 100 | 1369.787
SVM | ug/dscm | 100 | 696.0478 |  |  | 100 | 674.776 | 100 | 732.0473 | 100 | 694.2196 | 100 | 700.3476
LVM | ug/dscm | 100 | 656.6902 |  |  | 100 | 904.7434 | 100 | 536.3727 | 100 | 517.4428 | 100 | 652.853
Tier I Feedrate Limits
Chlorine | g/hr |  | 8870
Ash | g/hr |  | 6410
Antimony | g/hr |  | 6650
Arsenic | g/hr |  | 14.2
Mercury | g/hr |  | 1770
Silver | g/hr |  | 66500
Barium | g/hr |  | 1109000
Beryllium | g/hr |  | 5.7
Cadmium | g/hr |  | 11.45
Chromium (Tri) | g/hr |  | 22180000
Chromium (Hex) | g/hr |  | 10.46
Lead | g/hr |  | 2000
Thallium | g/hr |  | 11090

## process
Process Info
Cond Avg
741C1
Comb Temp | °F | 2117
Steam Prod Rate | lb/hr | 154300