## source
Source Description
Phase II ID No. | 765
EPA ID No. | IND006376362
Facility Name | GE Plastics, Mt. Vernon IN Facility
Facility Location
City | Mount Vernon
State | IN
Unit ID Name/No. | Boiler H530B (Unit 2)
Other Sister Facilities | None
Combustor | Liquid-fired boiler
Combustor Characteristics | Watertube boiler. Babcock & Wilcox Model 103-88 boiler, 70,000 lb/hr steam @ 195 psig
Capacity (MMBtu/hr) | 75
Soot Blowing | Yes, 5 min per day
APCS | None
APCS Characteristics | NA
Hazardous Wastes | Liq
Haz Waste Description | Liq wastes -- benzene byproduct, phenol distillation tar
Supplemental Fuel | Natural gas
Stack Characteristics | #764 and #765 boilers have a common stack
Diameter (ft) | 5
Height (ft) | 118
Gas Velocity (ft/sec) | 63.7
Gas Temperature (°F) | 529
Permitting Status | Tier I Adjusted for all metals, chlorine
HWC Burn Status (Date if Terminated)

## cond
Cond Description
765C1
Report Name/Date | Revised Recertification of Compliance of BIF Boilers H530A and H530B, GE Plastics Mt. Vernon Facility, February 1998
Report Prepare | Airtech Environmental Services, Inc.
Testing Firm | Planet Air Group
Testing Dates | 1998-02-12
Cond Dates | 1998-02-01
Condition Descr | CoC, max waste and ash feed
Content | PM, CO

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2 | 1 | 2 | 3 | Avg.
Sootblowing
1 | Condition 1
| PM |  | gr/dscf | y | 0.0292 | 0.034 | 0.0411 | 0.034767
| CO (RA) |  | ppmv | y | 13.9 | 12.7 | 12.8 | 13.1333
| CO (MHRA) |  | ppmv | y | 17.9 | 13.3 | 13.2 | 14.8

## feed
Feedstreams
* | 765C1 |  |  | R1 |  | R2 |  | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Description |  |  | Liq. Waste |  | Liq. Waste |  | Liq. Waste | Liq. Waste | Natural gas | Natural gas | Natural gas | Natural gas | Total | Total | Total | Total
| Feed Rate | scf/hr | [7 empty] | 1.086 | 0 | 0 | 362
| Feed Rate | lb/hr |  | 4714.4 |  | 4788 |  | 4788.1 | 4764
| Heating Value | Btu/lb | [6 empty] | 15107
| Thermal Feedrate | MMBtu/hr |  | 73.187 |  | 72.517 |  | 72.78 | 72 |  |  |  | 0.4
| Ash | wt % | [6 empty] | 0.117
| (Ash) | lb/hr |  | 5.67 |  | 5.46 |  | 5.747 | 5.626
| Chlorine | ppmw | nd | 100 | nd | 100 | nd | 100 | 100
| Antimony | ppmw | nd | 1 | nd | 1 | nd | 1 | 1
| Arsenic | ppmw | nd | 0.08 | nd | 0.08 | nd | 0.08 | 0.08
| Barium | ppmw | nd | 0.08 | nd | 0.08 | nd | 0.08 | 0.08
| Beryllium | ppmw | nd | 0.04 | nd | 0.04 | nd | 0.04 | 0.04
| Cadmium | ppmw | nd | 0.008 | nd | 0.008 | nd | 0.008 | 0.008
| Chromium | ppmw |  | 1.21 |  | 1.19 |  | 1.21 | 1.2
| Lead | ppmw | nd | 0.04 | nd | 0.04 | nd | 0.04 | 0.04
| Mercury | ppmw | nd | 0.02 | nd | 0.02 | nd | 0.02 | 0.02
| Silver | ppmw | nd | 0.08 | nd | 0.08 | nd | 0.08 | 0.08
| Thallium | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 | 0.1
| Stack Gas Flowrate | dscfm |  | 17518.7 |  | 17518.7 |  | 17518.7 | 17518.7
| Oxygen | % |  | 5.5 |  | 5.5 |  | 5.5 | 5.5
Flowrate and oxygen estimated based on total firing rate
| Thermal Feedrate | MMBtu/hr |  | 73.187 |  | 72.517 |  | 72.78 | 72 |  |  |  | 0.4 |  |  |  | 72.4
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 78.162 |  | 75.2671 |  | 79.2235 | 77.5555 |  |  |  |  | 78.162 | 75.2671 | 79.2235 | 77.5509
| Ash | gr/dscf |  | 0.034105 |  | 0.032842 |  | 0.034569 | 0.033841 |  |  |  | good ash mass balance!
| Chlorine | ug/dscm | nd | 6498.8881 | nd | 6600.347 | nd | 6600.4849 | 6567.2626 |  |  |  |  | 3249.444 | 3300.1735 | 3300.2424 | 3283.2867
| Antimony | ug/dscm | nd | 64.9889 | nd | 66.0035 | nd | 66.0048 | 65.6726
| Arsenic | ug/dscm | nd | 5.1991 | nd | 5.2803 | nd | 5.2804 | 5.2538
| Barium | ug/dscm | nd | 5.1991 | nd | 5.2803 | nd | 5.2804 | 5.2538
| Beryllium | ug/dscm | nd | 2.5996 | nd | 2.6401 | nd | 2.6402 | 2.6269
| Cadmium | ug/dscm | nd | 0.51991 | nd | 0.52803 | nd | 0.52804 | 0.52538
| Chromium | ug/dscm |  | 78.6365 |  | 78.5441 |  | 79.8659 | 78.8072
| Lead | ug/dscm | nd | 2.5996 | nd | 2.6401 | nd | 2.6402 | 2.6269
| Mercury | ug/dscm | nd | 1.2998 | nd | 1.3201 | nd | 1.3201 | 1.3135 |  |  |  |  | 0.64989 | 0.66003 | 0.66005 | 0.65666
| Silver | ug/dscm | nd | 5.1991 | nd | 5.2803 | nd | 5.2804 | 5.2538
| Thallium | ug/dscm | nd | 6.4989 | nd | 6.6003 | nd | 6.6005 | 6.5673
| SVM | ug/dscm |  | 1.5597 |  | 1.5841 |  | 1.5841 | 1.5761 |  |  |  |  | 1.5597 | 1.5841 | 1.5841 | 1.576
| LVM | ug/dscm |  | 82.5359 |  | 82.5043 |  | 83.8262 | 82.7475 |  |  |  |  | 82.5359 | 82.5043 | 83.8262 | 82.9555
BIF Feedrate Limits
| Antimony | g/hr | [6 empty] | 6246
| Arsenic | g/hr | [6 empty] | 2.9
| Barium | g/hr | [6 empty] | 1041064
| Beryllium | g/hr | [6 empty] | 1.7
| Cadmium | g/hr | [6 empty] | 2.3
| Chromium | g/hr | [6 empty] | 15.6
| Lead | g/hr | [6 empty] | 1874
| Mercury | g/hr | [6 empty] | 6246
| Silver | g/hr | [6 empty] | 62464
| Thallium | g/hr | [6 empty] | 10411
| Chlorine | g/hr | [6 empty] | 8329

## summ 1
Source Description Summary Sheet
Facility Name | City | State | EPA ID No. | Phase II ID No. | Comb Type | APCS | Waste Descr | Waste Type | Aux Fuel | Unit ID Name/No. | Sister Units | Capacity (MMBtu/hr)
GE Plastics, Mt. Vernon IN Facility | Mount Vernon | IN | IND006376362 | 765 | Liquid-fired boiler | None | Liq wastes -- benzene byproduct, phenol distillation tar | Liq | Natural gas | Boiler H530B (Unit 2) | None | 75

## summ 2
Emissions and Feedrate Data Summary Sheet -- condition averages, @ 7% O2
Cond ID | Facility Design/Operation | [5 empty] | Condition | Stack Gas Emissions | [13 empty] | Feedrate Characteristics | [17 empty] | APCD | Stack Gas Conditions |  |  |  | Individual Metal Feedrates | [19 empty] | Individual Metal Emissions
| APCS | System | HW | Aux | Heat Input Rate |  | Description | PM | HCl | Cl2 | TCl | D/F TEQ | D/F Total | Hg | SVM | LVM | CO | CO | HC | DRE |  | Hg |  |  |  | SVM |  |  |  | LVM |  |  |  | TCl |  |  | Ash |  |  | Temp | Flowrate | O2 | Moisture | Temp | Pb | ND | Cd | ND | As | ND | Be | ND | Cr | ND | Sb | ND | Ni | ND | Co | ND | Mn | ND | Se | ND | Pb | ND | Cd | ND | As | ND | Be | ND | Cr | ND | Cr(+6) | ND | Sb | ND | Ni | ND | Co | ND | Mn | ND | Se | ND
|  | Design | Type | Fuel | MM Btu/hr |  |  | gr/dscf | ppmv | ppmv | ppmv | ng/dscm | ng/dscm | µg/dscm | µg/dscm | µg/dscm | MHRA | RA | ppmv | max | min | HW | Other | Spike | ND | HW | Other | Spike | ND | HW | Other | Spike | ND | HW | Other | Spike | HW | Other | Spike |  | dscfm | % | % | °F | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | % | µg/dscm | %
|  |  |  | Type | HW | Other | [10 empty] | ppmv | ppmv |  | % | % | µg/dscm | µg/dscm | % | % | µg/dscm | µg/dscm | % | % | µg/dscm | µg/dscm | % | % | µg/dscm | µg/dscm | % | mg/dscm | mg/dscm | %
765C1 | None | Liquid-fired boiler | Liq | Natural gas | 72 | 0.4 | CoC, max waste and ash feed | 0.034767 | [8 empty] | 14.8 | 13.1333 |  |  |  | 0.65673 |  |  | 100 | 1.5761 |  |  |  | 82.7475 |  |  |  | 3283.6313 |  |  | 77.5555 |  |  |  | 17518.7 | 5.5 |  |  | 1.3135 | 100 | 0.26269 | 100 | 2.6269 | 100 | 1.3135 | 100 | 78.8072 | 0 | 32.8363 | 100
765 | None | Liquid-fired boiler | Liq | Natural gas | 72 | 0.4 | Baseline | 0.034767 | [8 empty] | 14.8 | 13.1333 |  |  |  | 0.65673 |  |  | 100 | 1.5761 |  |  |  | 82.7475 |  |  |  | 3283.6313 |  |  | 77.5555 |  |  |  | 17518.7 | 5.5 |  |  | 1.3135 | 100 | 0.26269 | 100 | 2.6269 | 100 | 1.3135 | 100 | 78.8072 | 0 | 32.8363 | 100