## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 774
EPA ID No. | TXD058275769
Facility Name | Equistar Chemicals, LP - Channelview Complex
Facility Location
City | Channelview
State | TX
Unit ID Name/No. | Boiler No. 3
Other Sister Facilities | Boiler No.1,2,4
Number of Sister Facilities | 3
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler. 230 MMBtu/hr watertube boiler
Capacity (MMBtu/hr) | 230
Soot Blowing | Yes, 13 minute duration
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics | NA
Hazardous Wastes | Liq
Haz Waste Description | T-303 bottoms, IPOH
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 6.5
Height (ft) | 63
Gas Velocity (ft/sec) | 52.9
Gas Temperature (°F) | 441
Permitting Status | Tier IA for metals and chlorine
HWC Burn Status (Date if Terminated)

## cond
Cond Description
774C1
Report Name/Date | Certification of Compliance Forms, November 1998
Report Prepare | Waste Min Inc.
Testing Firm | Waste Min Inc.
Testing Dates | 1998-09-22
Cond Dates | 1998-09-01
Condition Descr | CoC; max feeds for T-303 bottoms and IPOH
Content | PM, Cl2, CO emissions; metals and chlorine in feedstreams
774C2
Report Name/Date | Certification of Compliance Forms, November 1998
Report Prepare | Waste Min Inc.
Testing Firm | Waste Min Inc.
Testing Dates | 1998-09-23
Cond Dates | 1998-09-01
Condition Descr | CoC; min combustion temperature
Content | CO

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
Sootblow
1 | 774C1 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0248 | 0.0228 | 0.0375 | 0.028367
| CO (RA) | E1 | ppmv | y | 6 | 4 | 3 | 4.3333
| CO (MHRA) | E1 | ppmv | y | 7 | 5 | 3 | 5
| Cl2 |  | g/hr |  | 213 | 310 | 266 | 263
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 51467 | 51467 | 51467 | 51467
| O2 |  | % |  | 7 | 7 | 7 | 7
| Moisture |  | % |  |  |  |  | 15.6
| Temperature |  | °F |  |  |  |  | 441
| Cl2 | E1 | ppmv | y | 0.81244 | 1.1824 | 1.0146 | 1.0032
| Total Chlorine | E1 | ppmv | y | 1.6249 | 2.3649 | 2.0292 | 2.0063
2 | 774C2 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) |  | ppmv | y | 15 | 16 | 20 | 17
| CO (MHRA) |  | ppmv | y | 37 | 17 | 23 | 25.6667

## feed
Feedstreams
* | 774C1 |  | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  | F1 | F1 | F1 | F1 | F2 | F2 | F2 | F2 |  |  |  |  | F3 | F3 | F3 | F3 | F4 | F4 | F4 | F4 | F5 | F5 | F5 | F5
| Feed Class |  | Liq HW | Liq HW | Liq HW | Liq HW | Liq HW | Liq HW | Liq HW | Liq HW |  |  |  |  | NG | NG | NG | NG | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Class 2 | [9 empty] | HW | HW | HW | HW | MF | MF | MF | MF | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feedstream Description |  | T-303 bottoms | T-303 bottoms | T-303 bottoms | T-303 bottoms | IPOH | IPOH | IPOH | IPOH |  |  |  |  | Nat gas | Nat gas | Nat gas | Nat gas | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Rate | g/hr | 633704 | 740937 | 688865 | 687835.3333 | 2017948 | 2265290 | 2265290 | 2182843 |  |  |  |  | 2774613 | 2774505 | 2762213 | 2770443.6667 | 197875 | 207707 | 214138 | 206573.3333 |  |  |  | 3077251.6667
| Thermal Feedrate | MMBtu/hr | 17.16 | 24 | 23.518 | 21.6333 | 55.56 | 64.366 | 64.365 | 61.4667 | 72.72 | 88.366 | 87.883 | 83.1 | 153 | 153.33 | 152.648 | 153 | 0.4 | 0.519 | 0.535 | 0.5 | 226.12 | 242.215 | 241.066 | 236.6
| Heating Value | Btu/lb |  |  |  | 14250 |  |  |  | 12725 | [7 empty] | 25089 |  |  |  | 500
| Density | g/ml |  |  |  | 0.72 |  |  |  | 0.81 | [11 empty] | 1.01
| Ash | g/hr | 222 | 593 | 344 | 386.3333 | 404 | 453 | 566 | 474.3333 |  |  |  |  | 5 | 5 | 5 | 5 | 10210 | 12379 | 10621 | 11070 |  |  |  | 11935.6667
| Chlorine | g/hr | 3 | 72 | 62 | 45.6667 | 188 | 211 | 179 | 192.6667 |  |  |  |  | 5 | 5 | 5 | 5 | 17 | 22 | 20 | 19.6667 |  |  |  | 263
| Antimony | g/hr | 1.9 | 2.22 | 2.07 | 2.0633 | 6.05 | 6.8 | 6.8 | 6.55 |  |  |  |  | 0.02 | 0.2 | 0.02 | 0.02 | 0.59 | 0.62 | 0.64 | 0.61667 |  |  |  | 9.25
| Arsenic | g/hr | 0.32 | 0.37 | 0.34 | 0.34333 | 1.01 | 1.13 | 1.13 | 1.09 |  |  |  |  | 0.02 | 0.2 | 0.02 | 0.02 | 0.1 | 0.1 | 0.11 | 0.1 |  |  |  | 1.5533
| Barium | g/hr | 0.16 | 0.19 | 0.17 | 0.17333 | 0.5 | 0.57 | 0.57 | 0.54667 |  |  |  |  | 0.37 | 0.37 | 0.37 | 0.37 | 0.05 | 1.35 | 0.05 | 0.48333 |  |  |  | 1.5733
| Beryllium | g/hr | 0.16 | 0.19 | 0.17 | 0.17333 | 0.5 | 0.57 | 0.57 | 0.54667 |  |  |  |  | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 |  |  |  | 0.77
| Cadmium | g/hr | 0.16 | 0.19 | 0.17 | 0.17333 | 0.5 | 0.57 | 0.57 | 0.54667 |  |  |  |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 0.05 | 0.05 | 0.05 |  |  |  | 0.78
| Chromium | g/hr | 0.32 | 0.37 | 0.34 | 0.34333 | 1.01 | 1.13 | 1.13 | 1.09 |  |  |  |  | 0.13 | 0.13 | 0.13 | 0.13 | 0.1 | 0.1 | 0.11 | 0.10333 |  |  |  | 1.6667
| Lead | g/hr | 0.32 | 0.37 | 0.34 | 0.34333 | 1.01 | 1.13 | 1.13 | 1.09 |  |  |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.11 | 0.10333 |  |  |  | 1.5567
| Mercury | g/hr | 0.17 | 0.21 | 0.09 | 0.15667 | 0.25 | 0.28 | 0.28 | 0.27 |  |  |  |  | 0 | 0 | 0 | 0 | 0.02 | 0.03 | 0.03 | 0.0266 |  |  |  | 0.45327
| Silver | g/hr | 0.16 | 0.19 | 0.17 | 0.17 | 0.5 | 0.57 | 0.57 | 0.54667 |  |  |  |  | 0.09 | 0.09 | 0.09 | 0.09 | 0.07 | 0.05 | 0.05 | 0.056667 |  |  |  | 0.86333
| Thallium | g/hr | 0.32 | 0.37 | 0.34 | 0.34 | 1.01 | 1.13 | 1.13 | 1.09 |  |  |  |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.1 | 0.1 | 0.11 | 0.10333 |  |  |  | 1.5633
| Stack Gas Flowrate | dscfm | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 |  |  |  |  | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 | 51467 | 51467
| Oxygen | % | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  |  |  |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
| Estimated Firing Rate | MMBtu/hr | [23 empty] | 228.7422
Feedrate MTEC Calculations
| Ash | mg/dscm | 2.5403 | 6.7856 | 3.9363 | 4.4207 | 4.6229 | 5.1836 | 6.4766 | 5.4277 | 7.1632 | 11.9692 | 10.413 | 9.8485 | 0.057214 | 0.057214 | 0.057214 | 0.057214 | 116.8313 | 141.6508 | 121.5343 | 126.6721 | 124.0517 | 153.6772 | 132.0045 | 136.5778
| Chlorine | ug/dscm | 34.3285 | 823.8838 | 709.4555 | 522.5559 | 2151.2521 | 2414.4372 | 2048.2666 | 2204.652 | 2185.5806 | 3238.321 | 2757.7221 | 2727.2079 | 57.2142 | 57.2142 | 57.2142 | 57.2142 | 194.5281 | 251.7423 | 228.8566 | 225.0423 | 2437.3229 | 3547.2774 | 3043.7929 | 3009.4644
| Antimony | ug/dscm | 21.7414 | 25.4031 | 23.6867 | 23.6104 | 69.2291 | 77.8112 | 77.8112 | 74.9505 | 90.9705 | 103.2143 | 101.4979 | 98.5609 | 0.22886 | 2.2886 | 0.22886 | 0.22886 | 6.7513 | 7.0946 | 7.3234 | 7.0564 | 97.9506 | 112.5975 | 109.0502 | 106.5328
| Arsenic | ug/dscm | 3.6617 | 4.2338 | 3.8906 | 3.9287 | 11.5573 | 12.9304 | 12.9304 | 12.4727 | 15.219 | 17.1642 | 16.821 | 16.4014 | 0.22886 | 2.2886 | 0.22886 | 0.22886 | 1.1443 | 1.1443 | 1.2587 | 1.1443 | 16.5921 | 20.5971 | 18.3085 | 18.4992
| Barium | ug/dscm | 1.8309 | 2.1741 | 1.9453 | 1.9834 | 5.7214 | 6.5224 | 6.5224 | 6.2554 | 7.5523 | 8.6966 | 8.4677 | 8.2388 | 4.2338 | 4.2338 | 4.2338 | 4.2338 | 0.57214 | 15.4478 | 0.57214 | 5.5307 | 12.3583 | 28.3782 | 13.2737 | 18.0034
| Beryllium | ug/dscm | 1.8309 | 2.1741 | 1.9453 | 1.9834 | 5.7214 | 6.5224 | 6.5224 | 6.2554 | 7.5523 | 8.6966 | 8.4677 | 8.2388 | 0 | 0 | 0 | 0 | 0.57214 | 0.57214 | 0.57214 | 0.57214 | 8.1244 | 9.2687 | 9.0398 | 8.811
| Cadmium | ug/dscm | 1.8309 | 2.1741 | 1.9453 | 1.9834 | 5.7214 | 6.5224 | 6.5224 | 6.2554 | 7.5523 | 8.6966 | 8.4677 | 8.2388 | 0.11443 | 0.11443 | 0.11443 | 0.11443 | 0.57214 | 0.57214 | 0.57214 | 0.57214 | 8.2388 | 9.3831 | 9.1543 | 8.9254
| Chromium | ug/dscm | 3.6617 | 4.2338 | 3.8906 | 3.9287 | 11.5573 | 12.9304 | 12.9304 | 12.4727 | 15.219 | 17.1642 | 16.821 | 16.4014 | 1.4876 | 1.4876 | 1.4876 | 1.4876 | 1.1443 | 1.1443 | 1.2587 | 1.1824 | 17.8508 | 19.7961 | 19.5672 | 19.0714
| Lead | ug/dscm | 3.6617 | 4.2338 | 3.8906 | 3.9287 | 11.5573 | 12.9304 | 12.9304 | 12.4727 | 15.219 | 17.1642 | 16.821 | 16.4014 | 0.22886 | 0.22886 | 0.22886 | 0.22886 | 1.1443 | 1.1443 | 1.2587 | 1.1824 | 16.5921 | 18.5374 | 18.3085 | 17.8127
| Mercury | ug/dscm | 1.9453 | 2.403 | 1.0299 | 1.7927 | 2.8607 | 3.204 | 3.204 | 3.0896 | 4.806 | 5.607 | 4.2338 | 4.8823 | 0 | 0 | 0 | 0 | 0.22886 | 0.34328 | 0.34328 | 0.30438 | 5.0348 | 5.9503 | 4.5771 | 5.1874
| Silver | ug/dscm | 1.8309 | 2.1741 | 1.9453 | 1.9453 | 5.7214 | 6.5224 | 6.5224 | 6.2554 | 7.5523 | 8.6966 | 8.4677 | 8.2007 | 1.0299 | 1.0299 | 1.0299 | 1.0299 | 0.801 | 0.57214 | 0.57214 | 0.64843 | 9.3831 | 10.2985 | 10.0697 | 9.9171
| Thallium | ug/dscm | 3.6617 | 4.2338 | 3.8906 | 3.8906 | 11.5573 | 12.9304 | 12.9304 | 12.4727 | 15.219 | 17.1642 | 16.821 | 16.3632 | 0.34328 | 0.34328 | 0.34328 | 0.34328 | 1.1443 | 1.1443 | 1.2587 | 1.1824 | 16.7065 | 18.6518 | 18.423 | 17.9271
| SVM | ug/dscm | 5.4926 | 6.408 | 5.8358 | 5.9121 | 17.2787 | 19.4528 | 19.4528 | 18.7281 | 22.7712 | 25.8608 | 25.2887 | 24.6402 | 0.34328 | 0.34328 | 0.34328 | 0.34328 | 1.7164 | 1.7164 | 1.8309 | 1.7546 | 24.8309 | 27.9205 | 27.4628 | 26.7381
| LVM | ug/dscm | 9.1543 | 10.6418 | 9.7264 | 9.8408 | 28.8359 | 32.3832 | 32.3832 | 31.2008 | 37.9902 | 43.025 | 42.1096 | 41.0416 | 1.7164 | 3.7761 | 1.7164 | 1.7164 | 2.8607 | 2.8607 | 3.0896 | 2.8989 | 42.5673 | 49.6619 | 46.9156 | 46.3816
* | 774C2 |  | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  |  |  |  | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  | F1 | F1 | F1 | F1 | F2 | F2 | F2 | F2 |  |  |  |  | F3 | F3 | F3 | F3 | F4 | F4 | F4 | F4 | F5 | F5 | F5 | F5
| Feed Class |  | Liq HW | Liq HW | Liq HW | Liq HW | Liq HW | Liq HW | Liq HW | Liq HW |  |  |  |  | NG | NG | NG | NG | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Class 2 | [9 empty] | HW | HW | HW | HW | MF | MF | MF | MF | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feedstream Description |  | T-303 bottoms | T-303 bottoms | T-303 bottoms | T-303 bottoms | IPOH | IPOH | IPOH | IPOH |  |  |  |  | Nat gas | Nat gas | Nat gas | Nat gas | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Rate | g/hr |  |  |  |  | 1288120 | 1288120 | 1288120 | 1288120 |  |  |  |  | 1361985 | 1363423 |  | 1363000
| Thermal Feedrate | MMBtu/hr | [7 empty] | 36.1361 | [7 empty] | 75.2728
| Heating Value | Btu/lb | [7 empty] | 12725 | [7 empty] | 25089
BIF Feedrate Limits
| Antimony | g/hr |  |  |  | 13219
| Arsenic | g/hr |  |  |  | 101
| Barium | g/hr |  |  |  | 2203182
| Beryllium | g/hr |  |  |  | 185
| Cadmium | g/hr |  |  |  | 247
| Chromium | g/hr |  |  |  | 36.6
| Lead | g/hr |  |  |  | 3966
| Mercury | g/hr |  |  |  | 13219
| Silver | g/hr |  |  |  | 132190
| Thallium | g/hr |  |  |  | 22032
| Chlorine | g/hr |  |  |  | 17625

## process
Process Information
| Units | Cond Avg
774C1
No data reported
774C2
Combustion Chamber Temp | F | 1332