## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 776
EPA ID No. | GAD981237118
Facility Name | Monsanto (Nutrasweet Kelco Co.)
Facility Location
City | Augusta
State | GA
Unit ID Name/No. | Boiler 1 - WHRU 1
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Firetube boiler. John Zink 2-stage combustion boiler, forced draft, with 3 burner guns; 66 MM Btu/hr, 49,000 lb/hr steam with fire-tube heat recovery boiler; part of cooled boiler exhaust is returned to 2nd stage combustor inlet
Capacity (MMBtu/hr) | 66
Soot Blowing | None
APCS Detailed Acronym | QC/WS
APCS General Class | WQ,LEWS
APCS Characteristics | (Cooler/caustic scrubber)
Hazardous Wastes | Liq
Haz Waste Description | Liquid, primarily ester #1 and methanol, classed as D001 and D002; 42-51% ester #1, 10-17% methanol, 11-18% water, 9-22% acetic acid, and < 1% hydrochloric acid; 8.1 lb/gal and 7,100 Btu/lb
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft)
Height (ft) | 100
Gas Velocity (ft/sec)
Gas Temperature (°F) | 162
Permitting Status | Tier IA for all metals, except Cr; Tier III for Cr and chlorine
HWC Burn Status (Date if Terminated)

## cond
Cond Description
776C10
Report Name/Date | BIF Recerification of Compliance Test Report - Boilers 1 and 2; dated August 20, 1997
Report Prepar | B3 Systems, Inc
Testing Firm | METCO
Testing Dates | June 17-25, 1997
Cond Dates | 1997-06-01
Cond. Description | CoC; max feedrate
Content | PM, CO, HCl/Cl2, Cr emissions; metals, ash, Cl feed analysis
776C11
Report Name/Date | BIF Recerification of Compliance Test Report - Boilers 1 and 2; dated August 20, 1997
Report Prepar | B3 Systems, Inc
Testing Firm | METCO
Testing Dates | June 17-25, 1997
Cond Dates | 1997-06-01
Cond. Description | CoC; min combustion temperature
Content | CO emissions

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
10 | 776C10 |  |  |  | R1 | R2 | R3 | Cond Avg
| Sampling Train | (PM, HCl/Cl2) | E1
| Stack Gas Flowrate |  | dscfm |  | 13240 | 12903 | 13598 | 13247
| O2 |  | % |  | 1.8 | 2 | 1.8 | 1.8667
| Moisture |  | % |  | 35.12 | 34.27 | 32.41 | 33.9333
| Temperature |  | °F |  | 164 | 162 | 161 | 162.3333
| PM |  | gr/dscf | n | 0.0496 | 0.0574 | 0.0483
| HCl |  | ppmv | n | 2.85 | 3.96 | 2.69
| Cl2 |  | ppmv | n | 0.04 | 0.01 | 0.02
| PM | E1 | gr/dscf | y | 0.036167 | 0.042295 | 0.035219 | 0.037893
| CO (RA) | E1 | ppmv | y | 3 | 5 | 3 | 3.6667
| CO (MHRA) | E1 | ppmv | y | 3 | 5 | 3 | 3.6667
| HCl | E1 | ppmv | y | 2.0781 | 2.9179 | 1.9615 | 2.3192
| Cl2 | E1 | ppmv | y | 0.029167 | 0.0073684 | 0.014583 | 0.017039
| Total Chlorine | E1 | ppmv | y | 2.1365 | 2.9326 | 1.9906 | 2.3532
| Sampling Train | Cr | E2
| Stack Gas Flowrate |  | dscfm |  | 13352 | 13004 | 12906 | 13087.3333
| O2 |  | % |  | 2.3 | 2.2 | 3.2 | 2.5667
| Moisture |  | % |  | 32.41 | 33.55 | 32.79 | 32.9167
| Temperature |  | °F |  | 163 | 161 | 160 | 161.3333
| Chromium |  | µg/dscm | n | 3.1301 | 5.3666 | 6.6088 | 5.0352
| Chromium | E2 | µg/dscm | y | 2.3434 | 3.9964 | 5.1979 | 3.8459
| LVM | E2 | µg/dscm | y | 2.3434 | 3.9964 | 5.1979 | 3.8459
11 | 776C11 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) | E1 | ppmv | y | 3.9 | 3.7 | 3.9 | 3.8333
| CO (MHRA) | E1 | ppmv | y | 4 | 3 | 4 | 3.6667
| Sampling Train | CO | E1
| Stack Gas Flowrate |  | dscfm
| O2 |  | % |  | 11 | 10.7 | 10.7 | 10.8
| Moisture |  | %
| Temperature |  | °F

## feed
Feedstreams
* | 776C10 |  |  | R1 | R2 | R2 | Cond Avg | R1 | R2 | R2 | Cond Avg | R1 | R2 | R2 | Cond Avg
| Feedstream Number |  |  | F1 | F1 | F1 | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3
| Feed Class |  |  | Liq HW | Liq HW | Liq HW | Liq HW | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Class 2 |  |  | HW | HW | HW | HW | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feedstream Description |  |  | Liquid waste | Liquid waste | Liquid waste | Liq waste | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Rate |  | g/hr | 4540000 | 4530000 | 4620000 | 4563333.3333 | 255000 | 255000 | 255000 | 255000
| Density |  | g/ml | 0.97 | 0.98 | 0.99 | 0.98
| Ash |  | g/hr | 4540 | 4530 | 4620 | 4563.3333 | 31800 | 31800 | 31800 | 31800
| Chlorine |  | g/hr | 5910 | 5440 | 4530 | 5293.3333 | 20300 | 20200 | 20200 | 20233.3333
| Mercury |  | g/hr | 0.0909 | 0.0906 | 0.0924 | 0.0913
| Lead |  | g/hr | 0.114 | 0.113 | 0.116 | 0.11433
| Cadmium |  | g/hr | 0.114 | 0.113 | 0.116 | 0.11433
| Arsenic |  | g/hr | 0.5 | 0.227 | 0.508 | 0.41167
| Beryllium |  | g/hr | 0.114 | 0.113 | 0.116 | 0.11433
| Chromium |  | g/hr | 0.3 | 0.3 | 0.3 | 0.3 | 5.81 | 5.81 | 5.81 | 5.81
| Antimony |  | g/hr | 0.264 | 0.113 | 0.189 | 0.18867
| Stack Gas Flowrate |  | dscfm | 13240 | 12903 | 13598 | 13247 | 13240 | 12903 | 13598 | 13247
| O2 |  | % | 1.8 | 2 | 1.8 | 1.8667 | 1.8 | 2 | 1.8 | 1.8667
| Thermal Feedrate |  | MMBtu/hr | 67.1 | 60.9 | 64.2 | 64.0667 |  |  |  |  | 67.1 | 60.9 | 64.2 | 64.0667
| Estimated Firing Rate |  | MMBtu/hr | [8 empty] | 80.701 | 77.8276 | 82.883 | 80.4633
Feedrate MTEC Calculations
| Ash |  | mg/dscm | 147.2506 | 152.3506 | 145.9003 | 148.5005 | 1031.4027 | 1069.4812 | 1004.2485 | 1035.0442 | 1178.6533 | 1221.8319 | 1150.1488 | 1183.5446
| Chlorine |  | µg/dscm | 191685.2152 | 182955.2816 | 143058.0452 | 172566.1807 | 641076.8911 | 637918.8768 | 637918.8768 | 638971.5483 | 832762.1063 | 820874.1584 | 780976.922 | 811537.7289
| Mercury |  | µg/dscm | 2.9483 | 3.047 | 2.918 | 2.9711 |  |  |  |  | 2.9483 | 3.047 | 2.918 | 2.9711
| Lead |  | µg/dscm | 3.6975 | 3.8004 | 3.6633 | 3.7204 |  |  |  |  | 3.6975 | 3.8004 | 3.6633 | 3.7204
| Cadmium |  | µg/dscm | 3.6975 | 3.8004 | 3.6633 | 3.7204 |  |  |  |  | 3.6975 | 3.8004 | 3.6633 | 3.7204
| Arsenic |  | µg/dscm | 16.217 | 7.6343 | 16.0427 | 13.298 |  |  |  |  | 16.217 | 7.6343 | 16.0427 | 13.298
| Beryllium |  | µg/dscm | 3.6975 | 3.8004 | 3.6633 | 3.7204 |  |  |  |  | 3.6975 | 3.8004 | 3.6633 | 3.7204
| Chromium |  | µg/dscm | 9.7302 | 10.0894 | 9.474 | 9.7646 | 183.4806 | 183.4806 | 183.4806 | 183.4806 | 193.2108 | 193.5701 | 192.9547 | 193.2452
| Antimony |  | µg/dscm | 8.5626 | 3.8004 | 5.9686 | 6.1105 |  |  |  |  | 8.5626 | 3.8004 | 5.9686 | 6.1105
| SVM |  | µg/dscm | 7.395 | 7.6007 | 7.3266 | 7.4408 |  |  |  |  | 7.395 | 7.6007 | 7.3266 | 7.4408
| LVM |  | µg/dscm | 29.6447 | 21.5242 | 29.1801 | 26.783 | 183.4806 | 183.4806 | 183.4806 | 183.4806 | 213.1253 | 205.0048 | 212.6607 | 210.2636
* | 776C11
| Feedstream Number |  |  | F1 | F1 | F1 | F1
| Feed Class |  |  | Liq HW | Liq HW | Liq HW | Liq HW
| Feed Class 2 |  |  | HW | HW | HW | HW
| Feedstream Description |  |  | Liquid waste | Liquid waste | Liquid waste | Liq waste
| Feed Rate |  | g/hr | 1670000 | 1710000 | 1690000 | 1690000
| Ash |  | g/hr | 1670 | 1710 | 1690 | 1690
| Chlorine |  | g/hr | 1840 | 1890 | 1860 | 1863.3333
| Mercury |  | g/hr | 0.0335 | 0.0343 | 0.0339 | 0.0339
| Lead |  | g/hr | 0.0452 | 0.0531 | 0.0458 | 0.048033
| Cadmium |  | g/hr | 0.0418 | 0.0429 | 0.0424 | 0.042367
| Arsenic |  | g/hr | 0.251 | 0.291 | 0.0847 | 0.2089
| Beryllium |  | g/hr | 0.0418 | 0.0429 | 0.0424 | 0.042367
| Chromium |  | g/hr | 0.234 | 0.257 | 0.322 | 0.271
| Antimony |  | g/hr | 0.124 | 0.137 | 0.424 | 0.22833
| Stack Gas Flowrate |  | dscfm |  |  |  | NA
| O2 |  | % | 2.3 | 2.2 | 3.2 | 2.5667
| Thermal Feedrate |  | MMBtu/hr | 22.5 | 23.4 | 23.5 | 23.1333
| Estimated Firing Rate |  | MMBtu/hr
Feedrate MTEC Calculations
| Ash | need stack gas flowrate to
| Chlorine | make calculations
Mercury
Lead
Cadmium
Arsenic
Beryllium
Chromium
Antimony
SVM
LVM

## process
Process Information
Units
776C10 |  | Cond Avg
Steam Production Rate | klb/hr | 51.16
Comb Chamber Temperature | F | 2000
Scrubber Operation
Scrubber L/G Ratio | gpm/kacfm | 6.5
Scrubber Liquid Blowdown | gpm | 9.2
Scrubber pH |  | 6
776C11
Comb Chamber Temperature | F | 1041