## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 778
EPA ID No. | NCD042091975
Facility Name | Mallinckrodt Inc.
Facility Location
City | Raleigh
State | NC
Unit ID Name/No. | Boiler No.1
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler. Cleaver-Brooks Model D34 water-tube boiler, John Zink LoNOx burner LN-HIV-25, 18.6 million Btu/hr heat input, 15,000 lb/hr steam production @ 125 psi, rotary soot blower
Capacity (MMBtu/hr) | 18.6
Soot Blowing | Yes; once per day for 5 minutes
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics
Hazardous Wastes | Liq
Haz Waste Description | Liquid, aniline, K083
Supplemental Fuel | Natural gas (start up only)
Stack Characteristics
Diameter (ft) | 2.25
Height (ft) | 50
Gas Velocity (ft/sec) | 32.6
Gas Temperature (°F) | 636
Permitting Status | Tier I metals, chlorine (IA for Cr)
HWC Burn Status (Date if Terminated)

## cond
Cond Description
778C10
Report Name/Date | Recertification of Compliance Test Report for Boiler No. 1, 8/27/98; Compliance Emission Test Report - Boiler No. 1, 8/21/98.
Report Preparer | Compliance Strategies & Solutions
Testing Firm | DEECO Inc.
Testing Dates | 1998-07-09
Cond Dates | 1998-07-01
Cond. Description | CoC; max waste feedrate
Content | PM, CO, Cr/Cr+6 emissions; ash, Cl, and metals feeds
778C11
Report Name/Date | Recertification of Compliance Test Report for Boiler No. 1, 8/27/98; Compliance Emission Test Report - Boiler No. 1, 8/21/98.
Report Preparer | Compliance Strategies & Solutions
Testing Firm | DEECO Inc.
Testing Dates | July 10, 1998 and August 19-20, 1998
Cond Dates | 1998-07-01
Cond. Description | CoC; min comb temperature
Content | CO

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
Soot blow
10 | 778C10 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E2 | gr/dscf | y | 0.055 | 0.056 | 0.138 | 0.068
| CO (MHRA) | E2 | ppmv | y | 2.9 | 2.5 | 2.2 | 2.5333
| Chromium (Hex) |  | g/hr |  | 0.008 | 0.037 | 0.034 | 0.024
| Chromium |  | g/hr |  | 0.245 | 0.271 | 4.38 | 0.877
| Sampling Train | Cr+6 | E1
| Stack Gas Flowrate |  | dscfm |  | 3300 | 3200 | 3200 | 3233.3333
| O2 |  | % |  | 8.3 | 8.1 | 8.1 | 8.1667
| Moisture |  | % |  | 13.5 | 14 | 13.7 | 13.7333
| Temperature |  | °F |  | 624 | 639 | 645 | 636
| Sampling Train | PM | E2
| Stack Gas Flowrate |  | dscfm |  | 3100 | 3000 | 3200 | 3100
| O2 |  | % |  | 8.2 | 8 | 8.7 | 8.3
| Moisture |  | % |  | 13.3 | 16.6 | 12.8 | 14.2333
| Temperature |  | °F |  | 624 | 633 | 652 | 636.3333
| Chromium (Hex) | E1 | µg/dscm | y | 1.6623 | 7.8222 | 7.1222 | 5.5356
| Chromium | E1 | µg/dscm | y | 50.9079 | 57.2921 | 917.507 | 341.9023
| LVM | E1 | µg/dscm | y | 0 | 0 | 0 | 0
11 | 778C11 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (MHRA) |  | ppmv | y | 12.4 | 10.6 | 13.5 | 12.1667

## feed
Feedstreams
* | 778C10 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total
| Feedstream Description |  |  | K083 |  | K083 |  | K083 |  | K083 |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 771 |  | 771.2 |  | 771.2 |  | 771.13 |  | 8.57 |  | 8.49 |  | 8.54 |  | 8.53
| Heat Content | Btu/lb |  | 14476 |  | 14642 |  | 14570 |  | 14562.6667 |  | 467 |  | 327 |  | 298 |  | 364
| Ash | lb/hr |  | 0.38515 |  | 0.06163 |  | 0.077048 |  | 0.17461 |  | 1.7425 |  | 1.6346 |  | 1.7449 |  | 1.7073
| Chlorine | g/hr |  | 43.25 |  | 53.65 |  | 55.75 |  | 50.8833 |  | 0.2371 | nd | 0.258 | nd | 0.2363 |  | 0.2438
| Mercury | g/hr | nd | 0.03 | nd | 0.03 | nd | 0.03 | nd | 0.015 | nd | 0.0004 | nd | 0.0004 | nd | 0.0004 |  | 0.0004
| Lead | g/hr | nd | 0.2 | nd | 0.2 | nd | 0.2 | nd | 0.101 | nd | 0.002 | nd | 0.001 | nd | 0.002 |  | 0.0016667
| Cadmium | g/hr | nd | 0.2 | nd | 0.2 | nd | 0.2 | nd | 0.101 | nd | 0.002 |  | 0.002 | nd | 0.002 |  | 0.002
| Arsenic | g/hr | nd | 0.2 | nd | 0.2 | nd | 0.2 | nd | 0.101 | nd | 0.002 | nd | 0.002 | nd | 0.002 |  | 0.002
| Beryllium | g/hr | nd | 0.2 | nd | 0.2 | nd | 0.2 | nd | 0.101 | nd | 0.002 | nd | 0.002 | nd | 0.002 |  | 0.002
| Chromium | g/hr |  | 1.001 |  | 1.401 |  | 1.501 |  | 1.301 |  | 0.001 | nd | 0.002 | nd | 0.002 |  | 0.0016667
| Antimony | g/hr | nd | 0.2 | nd | 0.2 | nd | 0.2 | nd | 0.2 | nd | 0.002 | nd | 0.002 | nd | 0.002 |  | 0.002
| Stack Gas Flowrate | dscfm |  | 3200 |  | 3100 |  | 3200 |  | 3233.3333 |  | 3200 |  | 3100 |  | 3200 |  | 3233.3333
| O2 | % |  | 8.25 |  | 8.05 |  | 8.4 |  | 8.1667 |  | 8.25 |  | 8.05 |  | 8.4 |  | 8.1667
| Thermal Feedrate | MMBtu/hr |  | 11.161 |  | 11.2919 |  | 11.2364 |  | 11.2298 |  | 0.0040022 |  | 0.0027762 |  | 0.0025449 |  | 0.0031078 |  | 11.165 |  | 11.2947 |  | 11.2389 |  | 11.2329
| Estimated Firing Rate | MMBtu/hr | [23 empty] | 13.1728
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 35.2795 |  | 5.7373 |  | 7.1415 |  | 16.0528 |  | 159.607 |  | 152.1678 |  | 161.7317 |  | 157.8355 | 0 | 194.8865 | 0 | 157.9051 | 0 | 168.8732 |  | 173.8882
| Chlorine | µg/dscm |  | 8733.7439 |  | 11010.6452 |  | 11391.9705 |  | 10378.7865 |  | 47.8791 | 100 | 52.9496 | 100 | 48.2856 | 67.891 | 49.7048 | 0 | 8781.623 | 0.47859 | 11063.5948 | 0.42207 | 11440.2561 | 0.32359 | 10428.4913
| Mercury | µg/dscm | 100 | 6.0581 | 100 | 6.1569 | 100 | 6.1302 | 100 | 6.1151 | 100 | 0.080775 | 100 | 0.082092 | 100 | 0.081736 | 100 | 0.081534 | 100 | 6.1389 | 100 | 6.239 | 100 | 6.2119 | 100 | 6.1966
| Lead | µg/dscm | 100 | 40.3873 | 100 | 41.0462 | 100 | 40.8681 | 100 | 40.7672 | 100 | 0.40387 |  | 0.20523 | 100 | 0.40868 | 79.8355 | 0.33926 | 100 | 40.7911 | 99.5025 | 41.2514 | 100 | 41.2767 | 99.8336 | 41.1064
| Cadmium | µg/dscm | 100 | 40.3873 | 100 | 41.0462 | 100 | 40.8681 | 100 | 40.7672 | 100 | 0.40387 | 100 | 0.41046 | 100 | 0.40868 | 100 | 0.40767 | 100 | 40.7911 | 100 | 41.4567 | 100 | 41.2767 | 100 | 41.1748
| Arsenic | µg/dscm | 100 | 40.3873 | 100 | 41.0462 | 100 | 40.8681 | 100 | 40.7672 | 100 | 0.40387 | 100 | 0.41046 | 100 | 0.40868 | 100 | 0.40767 | 100 | 40.7911 | 100 | 41.4567 | 100 | 41.2767 | 100 | 41.1748
| Beryllium | µg/dscm | 100 | 40.3873 | 100 | 41.0462 | 100 | 40.8681 | 100 | 40.7672 | 100 | 0.40387 | 100 | 0.41046 | 100 | 0.40868 | 100 | 0.40767 | 100 | 40.7911 | 100 | 41.4567 | 100 | 41.2767 | 100 | 41.1748
| Chromium | µg/dscm |  | 202.1382 |  | 287.5287 |  | 306.7148 |  | 265.4606 |  | 0.20194 | 100 | 0.41046 | 100 | 0.40868 | 80.2232 | 0.34036 | 0 | 202.3401 | 0.14255 | 287.9391 | 0.13307 | 307.1234 | 0.10273 | 265.8009
| Antimony | µg/dscm | 100 | 40.3873 | 100 | 41.0462 | 100 | 40.8681 | 100 | 40.7672 | 100 | 0.40387 | 100 | 0.41046 | 100 | 0.40868 | 100 | 0.40767 | 100 | 40.7911 | 100 | 41.4567 | 100 | 41.2767 | 100 | 41.1748
| SVM | µg/dscm | 100 | 80.7745 | 100 | 82.0924 | 100 | 81.7361 | 100 | 81.5343 | 100 | 0.80775 | 66.6667 | 0.61569 | 100 | 0.81736 | 90.8412 | 0.74693 | 100 | 81.5823 | 99.7519 | 82.7081 | 100 | 82.5535 | 99.9169 | 82.2813
| LVM | µg/dscm | 28.551 | 282.9127 | 22.2099 | 369.6211 | 21.0416 | 388.4509 | 23.4973 | 346.9949 | 80 | 1.0097 | 100 | 1.2314 | 100 | 1.226 | 94.1757 | 1.1557 | 28.734 | 283.9224 | 22.4682 | 370.8525 | 21.29 | 389.6769 | 23.7319 | 348.1506
BIF Feedrate Limits
| Antimony | g/hr | [7 empty] | 893
| Arsenic | g/hr | [7 empty] | 6.84
| Barium | g/hr | [7 empty] | 148760
| Beryllium | g/hr | [7 empty] | 12.5
| Cadmium | g/hr | [7 empty] | 16.66
| Chromium | g/hr | [7 empty] | 90.15
| Lead | g/hr | [7 empty] | 268
| Mercury | g/hr | [7 empty] | 893
| Silver | g/hr | [7 empty] | 8926
| Thallium | g/hr | [7 empty] | 1488
| Chlorine | g/hr | [7 empty] | 1190

## process
Process Information
Cond ID No. | Units | Run | Run | Run | Avg
|  | 1 | 2 | 3
778C11
Comb Temperature | °F | 1750.4 | 1755.4 | 1764.6 | 1756.8