## list
source
cond
emiss 2
feed 2
process 2

## source
Source Description
Phase I ID No. | 824
EPA ID No. | NJD980753875
Facility Name | Pennwalt Corporation
Facility Location
City | Thorofare
State | NJ
Unit ID Name/No. | Isotron 142
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Onsite incinerator
Combustor Type | Liquid injection?
Combustor Characteristics
Capacity (MMBtu/hr)
Soot Blowing
APCS Detailed Acronym | QT/VS/PT/DM
APCS General Class | WQ, HEWS, LEWS
APCS Characteristics | Quench, venturi scrubber, packed tower, demister
Hazardous Wastes | Liq
Haz Waste Description | liquid and gas HW
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 0.66663
Height (ft) | 47.9977
Gas Velocity (ft/sec) | 15.8206
Gas Temperature (°F) | 67.5556
Permitting Status
HWC Burn Status (Date if Terminated)

## cond
Condition Description
824C1
| Report Name/Date | Trial Burn Test Report, Pennwalt Corporation, Isotron 142b Incinerator, Thorofare, New Jersey, June 1989, Volume 1 of 2, prepared by PEI Associates, Inc.
| Report Prepare | PEI
| Testing Firm | PEI
824C1 | Cond Descr | DCFE Trial Burn
824C1 | Testing Dates | June 20-22, 1989
824C1 | Cond Dates | 1989-06-01

## emiss 2
Stack Gas Emissions 2
| 824C1 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
824C1 | PM | E3 | gr/dscf | y |  | 0.0056001 |  | 0.0064001 |  | 0.0068001 |  | 0.0062667 | 0.0062667
824C1 | CO (RA) | E1 | ppmv | y |  | 8.5114 |  | 8.6978 |  | 5.1103 |  | 7.4398 | 7.4398
824C1 | HCl | E1 | ppmv | y |  | 2.4 |  | 2.3596 |  | 1.5909 |  | 2.1168 | 2.1168
| Total Chlorine | E1 | ppmv | y |  | 2.4 |  | 2.3596 |  | 1.5909 |  | 2.1168
824C1 | HF | E2 | ppmv | y | nd | 0.24 | nd | 0.23596 | nd | 0.23864 | 100 | 0.2382 | 0.2382
824C1 | Arsenic | E2 | ug/dscm | y |  | 23.3755 |  | 18.75 |  | 19.3967 |  | 20.5074 | 20.5074
824C1 | Barium | E2 | ug/dscm | y |  | 12.2117 |  | 13.0443 |  | 10.313 |  | 11.8563 | 11.8563
824C1 | Beryllium | E2 | ug/dscm | y | nd | 0.28212 | nd | 0.26895 | nd | 0.29168 | 100 | 0.28092 | 0.28092
824C1 | Cadmium | E2 | ug/dscm | y |  | 0.75164 |  | 5.3022 |  | 14.8131 |  | 6.9557 | 6.9557
824C1 | Chromium | E2 | ug/dscm | y |  | 54.8115 |  | 60.5147 |  | 91.879 |  | 69.0684 | 69.0684
824C1 | Lead | E2 | ug/dscm | y |  | 48.3631 |  | 8.5489 |  | 49.7938 |  | 35.5686 | 35.5686
824C1 | Mercury | E2 | ug/dscm | y |  | 0.73149 |  | 0.94518 |  | 0.62919 |  | 0.76862 | 0.76862
824C1 | Nickel | E2 | ug/dscm | y |  | 15.1941 |  | 26.3191 |  | 74.5866 |  | 38.6999 | 38.6999
824C1 | Selenium | E2 | ug/dscm | y |  | 4.9169 |  | 0.34003 |  | 0.38543 |  | 1.8808 | 1.8808
824C1 | Silver | E2 | ug/dscm | y | nd | 1.2494 |  | 10.8542 |  | 6.1253 |  | 6.0763 | 6.0763
| SVM | E2 | ug/dscm | y |  | 49.1147 |  | 13.8511 |  | 64.607 |  | 42.5243
| LVM | E2 | ug/dscm | y |  | 78.4691 |  | 79.5336 |  | 111.5674 |  | 89.8567
| Sampling Train | Halogens | E1
| Stack Gas Flowrate |  | dscfm |  |  | 1123 |  | 1073 |  | 1053
| O2 |  | % |  |  | 3.5 |  | 3.2 |  | 3.4
824C1 | Moisture |  | % |  |  | 2.1 |  | 1.8 |  | 2.2
| Temperature |  | °F |  |  | 66 |  | 66 |  | 67
| Sampling Train | Metals | E2
| Stack Gas Flowrate |  | dscfm |  |  | 1042 |  | 1093 |  | 1043
| O2 |  | % |  |  | 3.2 |  | 3.2 |  | 3.8
| Moisture |  | % |  |  | 1.5 |  | 1.7 |  | 1.5
| Temperature |  | °F |  |  | 68 |  | 68 |  | 69
| Sampling Train | Particulate | E3
| Stack Gas Flowrate |  | dscfm |  |  | 1097 |  | 1064 |  | 1028
| O2 |  | % |  |  | 3.5 |  | 3 |  | 3.2
| Moisture |  | % |  |  | 1.6 |  | 2 |  | 2.2
| Temperature |  | °F |  |  | 67 |  | 68 |  | 69
824C1 | 1,1,1-dichloroflouroethane | DRE | % |  |  | 99.992 |  | 99.994 |  | 99.994

## feed 2
Feedstream 2
| 824C1 |  |  |  | R1 |  | R2 |  | R3 |  | R1 |  | R2 |  | R3 |  | R1 |  | R2 |  | R3 | R1 | R2 | R3 |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 | [6 empty] | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Gaseous HW |  | Gaseous HW |  | Gaseous HW |  | Liq HW |  | Liq HW |  | Liq HW | [6 empty] | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 | [15 empty] | HW |  | HW |  | HW | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Gas |  | Gas |  | Gas |  | Liquid |  | Liquid |  | Liquid | [6 empty] | Nat gas | Nat gas | Nat gas |  | Total |  | Total |  | Total |  | Total
824C1 | Feedrate | lb/hr |  |  | 110 |  | 118 |  | 139 |  | 660 |  | 660 |  | 660 | [6 empty] | 32.3167 | 31.4833 | 31.5667
824C1 | Heating value | Btu/lb
824C1 | Ash | wt %
824C1 | Chlorine | ppmw |  |  | 131000 |  | 180000 |  | 202000 |  | 4900 |  | 6000 |  | 4700
824C1 | Arsenic | ppmw |  |  | 4.8 |  | 6.2 |  | 7.6 |  | 42 |  | 39 |  | 35
824C1 | Barium | ppmw |  |  | 0.61 |  | 0.8 |  | 0.8 |  | 1.1 |  | 1.5 |  | 0.9
824C1 | Beryllium | ppmw |  | 1 | 0.02 | 1 | 0.02 | 1 | 0.01 | 1 | 0.023 | 1 | 0.023 | 1 | 0.026
824C1 | Cadmium | ppmw |  | 1 | 0.03 | 1 | 0.02 | 1 | 0.02 |  | 0.27 | 1 | 0.05 | 1 | 0.056
824C1 | Chromium | ppmw |  |  | 0.15 |  | 0.09 |  | 0.08 |  | 21 |  | 23 |  | 32
824C1 | Fluorine | ppmw |  |  | 313000 |  | 286000 |  | 270000 |  | 667000 |  | 616000 |  | 650000
824C1 | Lead | ppmw |  | 1 | 0.47 | 1 | 0.41 | 1 | 0.33 |  | 2.8 |  | 3.3 |  | 1.9
824C1 | Mercury | ppmw |  |  | 0.01 | 1 | 0.01 | 1 | 0.01 |  | 0.03 |  | 0.03 |  | 0.05
824C1 | Nickel | ppmw |  | 1 | 0.28 | 1 | 0.25 | 1 | 0.02 |  | 54 |  | 58 |  | 87
824C1 | Selenium | ppmw |  | 1 | 0.02 | 1 | 0.02 | 1 | 0.01 | 1 | 0.029 | 1 | 0.028 | 1 | 0.032
824C1 | Silver | ppmw |  |  | 0.12 |  | 0.14 |  | 0.31 |  | 0.45 |  | 0.57 |  | 0.69
| Stack gas flowrate | dscfm |  |  | 1123 |  | 1073 |  | 1053 |  | 1123 |  | 1073 |  | 1053 | [6 empty] | 1123 | 1073 | 1053 | [7 empty] | 1053
| O2 | % |  |  | 3.5 |  | 3.2 |  | 3.4 |  | 3.5 |  | 3.2 |  | 3.4 | [6 empty] | 3.5 | 3.2 | 3.4 | [7 empty] | 3.4
| Estimated Firing Rate | MMBtu/hr | [29 empty] | 5.8834
Feedrate MTEC Calculations
| Chlorine | ug/dscm | y |  | 2744684.1761 |  | 4162756.3384 |  | 5671152.5979 |  | 615982.5556 |  | 776107.1139 |  | 626537.3374 | 0 | 3360666.7317 | 0 | 4938863.4524 | 0 | 6297689.9353 |  |  |  | 0 | 3360666.7317 | 0 | 4938863.4524 | 0 | 6297689.9353 | 0 | 4865740.0398
| Arsenic | ug/dscm | y |  | 100.5686 |  | 143.3838 |  | 213.3701 |  | 5279.8505 |  | 5044.6962 |  | 4665.7036 | 0 | 5380.4191 | 0 | 5188.0801 | 0 | 4879.0737 |  |  |  | 0 | 5380.4191 | 0 | 5188.0801 | 0 | 4879.0737 | 0 | 5149.1909
| Barium | ug/dscm | y |  | 12.7806 |  | 18.5011 |  | 22.46 |  | 138.2818 |  | 194.0268 |  | 119.9752 | 0 | 151.0624 | 0 | 212.5279 | 0 | 142.4352 |  |  |  | 0 | 151.0624 | 0 | 212.5279 | 0 | 142.4352 | 0 | 168.6752
| Beryllium | ug/dscm | y | 100 | 0.41904 | 100 | 0.46253 | 100 | 0.28075 | 100 | 2.8913 | 100 | 2.9751 | 100 | 3.466 | 100 | 3.3104 | 100 | 3.4376 | 100 | 3.7467 |  |  |  | 100 | 3.3104 | 100 | 3.4376 | 100 | 3.7467 | 100 | 3.4982
| Cadmium | ug/dscm | y | 100 | 0.62855 | 100 | 0.46253 | 100 | 0.5615 |  | 33.9419 | 100 | 6.4676 | 100 | 7.4651 | 1.8182 | 34.5704 | 100 | 6.9301 | 100 | 8.0266 |  |  |  | 1.8182 | 34.5704 | 100 | 6.9301 | 100 | 8.0266 | 31.4681 | 16.5091
| Chromium | ug/dscm | y |  | 3.1428 |  | 2.0814 |  | 2.246 |  | 2639.9252 |  | 2975.0773 |  | 4265.7861 | 0 | 2643.068 | 0 | 2977.1586 | 0 | 4268.0321 |  |  |  | 0 | 2643.068 | 0 | 2977.1586 | 0 | 4268.0321 | 0 | 3296.0863
| Fluorine | ug/dscm | y |  | 6557909.5201 |  | 6614157.2933 |  | 7580253.4725 |  | 83849053.9915 |  | 79680330.3647 |  | 86648780.7006 | 0 | 90406963.5116 | 0 | 86294487.6579 | 0 | 94229034.1731 |  |  |  | 0 | 90406963.5116 | 0 | 86294487.6579 | 0 | 94229034.1731 | 0 | 90310161.7809
| Lead | ug/dscm | y | 100 | 9.8473 | 100 | 9.4818 | 100 | 9.2648 |  | 351.99 |  | 426.8589 |  | 253.2811 | 2.7215 | 361.8374 | 2.173 | 436.3407 | 3.5288 | 262.5458 |  |  |  | 2.7215 | 361.8374 | 2.173 | 436.3407 | 3.5288 | 262.5458 | 2.6957 | 353.5746
| Mercury | ug/dscm | y |  | 0.20952 | 100 | 0.23126 | 100 | 0.28075 |  | 3.7713 |  | 3.8805 |  | 6.6653 | 0 | 3.9808 | 5.6244 | 4.1118 | 4.0419 | 6.946 |  |  |  | 0 | 3.9808 | 5.6244 | 4.1118 | 4.0419 | 6.946 | 3.4046 | 5.0129
| Nickel | ug/dscm | y | 100 | 5.8665 | 100 | 5.7816 | 100 | 0.5615 |  | 6788.3792 |  | 7502.3688 |  | 11597.606 | 0.086345 | 6794.2457 | 0.077004 | 7508.1504 | 0.0048413 | 11598.1675 |  |  |  | 0.086345 | 6794.2457 | 0.077004 | 7508.1504 | 0.0048413 | 11598.1675 | 0.04714 | 8633.5212
| Selenium | ug/dscm | y | 100 | 0.41904 | 100 | 0.46253 | 100 | 0.28075 | 100 | 3.6456 | 100 | 3.6218 | 100 | 4.2658 | 100 | 4.0646 | 100 | 4.0844 | 100 | 4.5465 |  |  |  | 100 | 4.0646 | 100 | 4.0844 | 100 | 4.5465 | 100 | 4.2318
| Silver | ug/dscm | y |  | 2.5142 |  | 3.2377 |  | 8.7033 |  | 56.5698 |  | 73.7302 |  | 91.981 | 0 | 59.084 | 0 | 76.9679 | 0 | 100.6843 |  |  |  | 0 | 59.084 | 0 | 76.9679 | 0 | 100.6843 | 0 | 78.9121
| SVM | ug/dscm | y |  | 10.4759 |  | 9.9444 |  | 9.8263 |  | 385.9319 |  | 433.3265 |  | 260.7462 | 2.6427 | 396.4078 | 3.7025 | 443.2708 | 6.3907 | 270.5724 |  |  |  | 2.6427 | 396.4078 | 3.7025 | 443.2708 | 6.3907 | 270.5724 | 3.9792 | 370.0837
| LVM | ug/dscm | y |  | 104.1304 |  | 145.9277 |  | 215.8968 |  | 7922.6671 |  | 8022.7486 |  | 8934.9557 | 0.041242 | 8026.7974 | 0.042083 | 8168.6763 | 0.040944 | 9150.8525 |  |  |  | 0.041242 | 8026.7974 | 0.042083 | 8168.6763 | 0.040944 | 9150.8525 | 0.041405 | 8448.7754

## process 2
Process Information 2
|  | 824C1 |  | R1 | R2 | R3
824C1 | 82410 | Combustion Temperature | F | 2089 | 2094 | 2102
824C1 | 82410 | WS Temperature | F | 89 | 88 | 90
824C1 | 82411 | WS Pressure Drop | in H2O | 62 | 62 | 60