## list
source
cond
emiss
feed
process
df c3

## source
Source Description
Phase II ID No. | 843
EPA ID No. | TXD008092793
Facility Name | Dow Chemical Company
Facility Location
City | Freeport
State | TX
Unit ID Name/No. | B-902
Other Sister Facilities | B-901, B-903
Number of Sister Facilities | 2
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler. Direct fired combustion chamber, Combusion Engineering, capacity of 229 MMBtu/hr, operated @ 1700-2200F, soot blowing capabilities
Capacity (MMBtu/hr) | 229
Soot Blowing | None
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics | N/A
Hazardous Wastes | Liq
Haz Waste Description | Liquid wastes (Heavy Oils)
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 5.5
Height (ft) | 52
Gas Velocity (ft/sec) | 21.2
Gas Temperature (°F)
Permitting Status | Tier l for metals and HCl/Cl2
HWC Burn Status (Date if Terminated)

## cond
Cond Description
843C1
Report Name/Date | B-902 Trial Burn and Risk Burn Report, October 9 and 12, 1998
Report Prepare | Focus Environmental, Inc.
Testing Firm | METCO Environmental
Testing Dates | July 15-16, 1998
Cond Dates | 1998-07-01
Condition Descr | Trial burn, max waste feed rate, max comb gas velocity
Content | PM, DRE for POHC (acetophenone)
843C2
Report Name/Date | B-902 Trial Burn and Risk Burn Report, October 9 and 12, 1998
Report Prepare | Focus Environmental, Inc.
Testing Firm | METCO Environmental
Testing Dates | 1998-07-14
Cond Dates | 1998-07-01
Condition Descr | Trial burn, min comb temp
Content | DRE for POHC (acetophenone)
843C3
Report Name/Date | B-902 Trial Burn and Risk Burn Report, October 9 and 12, 1998
Report Prepare | Focus Environmental, Inc.
Testing Firm | METCO Environmental
Testing Dates | February 10-11, 1998
Cond Dates | 1998-02-01
Condition Descr | Risk burn, slightly above normal operating conditions
Content | PCDD/F, metals

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
1 | 843C1 | Trial Burn |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.013 |  | 0.012 |  | 0.026 |  | 0.017
| CO (MHRA) | E1 | ppmv | y |  | 45.55 |  | 13.53 |  | 60.21 |  | 39.7633
| CO (RA) | E1 | ppmv | y |  | 20.25 |  | 6.8 |  | 29.45 |  | 18.8333
| POHC DRE | Acetophenone
| Feedrate |  | ug/hr |  |  | 410000.001 |  | 420000.0011 |  | 500000.0013
| Emission Rate | E2 | ug/hr |  |  | 0.0082 |  | 0.0084 |  | 0.01
| DRE | E2 | % |  |  | 100 |  | 100 |  | 100
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  |  | 32300 |  | 32900 |  | 32500 |  | 32600
| O2 |  | % |  |  | 5.2 |  | 5.1 |  | 5 |  | 5.1
| Moisture |  | %
| Temperature |  | °F
| Sampling Train | DRE | E2
| Stack Gas Flowrate |  | dscfm |  |  | 33000 |  | 32200 |  | 32800 |  | 32700
| O2 |  | %
| Moisture |  | %
| Temperature |  | °F
2 | 843C2 | Trial Burn |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| CO (MHRA) | E1 | ppmv | y |  | 26.87 |  | 15.75 |  | 26.83 |  | 23.15
| CO (RA) | E1 | ppmv | y |  | 17.99 |  | 14.58 |  | 19.91 |  | 17.4933
| POHC DRE | Acetophenone
| Feedrate |  | units? |  |  | 199999.9998 |  | 199999.9996 |  | 197499.9998
| Emission Rate | E1 | units? |  |  | 0.008 |  | 0.006 |  | 0.0079
| DRE | E1 | % |  |  | 100 |  | 100 |  | 100
| Sampling Train | DRE | E1
| Stack Gas Flowrate |  | dscfm |  |  | 32400 |  | 32200 |  | 33200 |  | 32600
| O2 |  | %
| Moisture |  | %
| Temperature |  | °F
3 | 843C3 | Risk Burn |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| CO (MHRA) | E1 | ppmv | y |  | 6.8 |  | 6.7 |  | 6.78 |  | 6.76
| CO (RA) | E1 | ppmv | y |  | 6.64 |  | 6.5 |  | 6.68 |  | 6.6067
| Antimony |  | µg/dscf |  | nd | 0.0052 | nd | 0.0056 | nd | 0.0057
| Arsenic |  | µg/dscf |  | nd | 0.011 | nd | 0.0092 | nd | 0.013
| Barium |  | µg/dscf |  |  | 0 |  | 0 |  | 0.158
| Beryllium |  | µg/dscf |  | nd | 0.00063 | nd | 0.00069 | nd | 0.0007
| Cadmium |  | µg/dscf |  | nd | 0.0034 | nd | 0.0037 | nd | 0.0076
| Chromium |  | µg/dscf |  |  | 0.177 |  | 0.211 |  | 0.223
| Cobalt |  | µg/dscf |  | nd | 0.014 | nd | 0.021 | nd | 0.016
| Copper |  | µg/dscf |  |  | 0 |  | 0 |  | 0
| Lead |  | µg/dscf |  | nd | 0.0085 | nd | 0.019 | nd | 0.031
| Manganese |  | µg/dscf |  |  | 0.168 |  | 0.106 |  | 0.0189
| Mercury |  | µg/dscf |  | nd | 0.0019 | nd | 0.0021 | nd | 0.6
| Molybdenum |  | µg/dscf |  | nd | 0.14 | nd | 0.14 | nd | 0.14
| Nickel |  | µg/dscf |  | nd | 0.021 | nd | 0.023 | nd | 0.023
| Selenium |  | µg/dscf |  | nd | 0.0091 | nd | 0.015 | nd | 0.01
| Silver |  | µg/dscf |  | nd | 0.0012 | nd | 0.0028 | nd | 0.0014
| Thallium |  | µg/dscf |  | nd | 0.0079 | nd | 0.0086 | nd | 0.0088
| Vanadium |  | µg/dscf |  | nd | 0.0074 | nd | 0.008 | nd | 0.0082
| Antimony | E1 | µg/dscm | y | nd | 0.18375 | nd | 0.19509 | nd | 0.19314 | 100 | 0.19066
| Arsenic | E1 | µg/dscm | y | nd | 0.38869 | nd | 0.32051 | nd | 0.44049 | 100 | 0.38323
| Barium | E1 | µg/dscm | y |  | 0 |  | 0 |  | 5.3536 |  | 1.7845
| Beryllium | E1 | µg/dscm | y | nd | 0.022261 | nd | 0.024038 | nd | 0.023718 | 100 | 0.023339
| Cadmium | E1 | µg/dscm | y | nd | 0.12014 | nd | 0.1289 | nd | 0.25751 | 100 | 0.16885
| Chromium | E1 | µg/dscm | y |  | 6.2544 |  | 7.3508 |  | 7.556 |  | 7.0538
| Cobalt | E1 | µg/dscm | y | nd | 0.4947 | nd | 0.7316 | nd | 0.54214 | 100 | 0.58948
| Copper | E1 | µg/dscm | y |  | 0 |  | 0 |  | 0 |  | 0
| Lead | E1 | µg/dscm | y | nd | 0.30035 | nd | 0.66192 | nd | 1.0504 | 100 | 0.67089
| Manganese | E1 | µg/dscm | y |  | 5.9364 |  | 3.6928 |  | 0.6404 |  | 3.4232
| Mercury | E1 | µg/dscm | y | nd | 0.067138 | nd | 0.07316 | nd | 20.3301 | 100 | 6.8235
| Molybdenum | E1 | µg/dscm | y | nd | 4.947 | nd | 4.8773 | nd | 4.7437 | 100 | 4.856
| Nickel | E1 | µg/dscm | y | nd | 0.74205 | nd | 0.80127 | nd | 0.77932 | 100 | 0.77421
| Selenium | E1 | µg/dscm | y | nd | 0.32155 | nd | 0.52257 | nd | 0.33884 | 100 | 0.39432
| Silver | E1 | µg/dscm | y | nd | 0.042403 | nd | 0.097546 | nd | 0.047437 | 100 | 0.062462
| Thallium | E1 | µg/dscm | y | nd | 0.27915 | nd | 0.29961 | nd | 0.29818 | 100 | 0.29231
| Vanadium | E1 | µg/dscm | y | nd | 0.26148 | nd | 0.2787 | nd | 0.27785 | 100 | 0.27268
| SVM | E1 | µg/dscm | y | 100 | 0.42049 | 100 | 0.79082 | 100 | 1.3079 | 100 | 0.83974
| LVM | E1 | µg/dscm | y | 6.1655 | 6.6654 | 4.4773 | 7.6954 | 5.7879 | 8.0202 | 5.4497 | 7.4603
| Sampling Train | Metals | E1
| Stack Gas Flowrate |  | dscfm |  |  | 17212 |  | 16546 |  | 16149 |  | 16635.6667
| O2 |  | %
| Moisture |  | %
| Temperature |  | °F
| Sampling Train | PCDD/PCDF | E2
| Stack Gas Flowrate |  | dscfm |  |  | 16900 |  | 17000 |  | 16900 |  | 16933.3333
| O2 |  | % |  |  | 7 |  | 6.8 |  | 6.4 |  | 6.7333
| Moisture |  | %
| Temperature |  | °F
| Particle Size Distribution | in microns
| 0.2-0.5 |  | % wt |  |  | 19.9
| 0.5-0.9 |  |  |  |  | 15.2
| 0.9-1.3 |  |  |  |  | 8.5
| 1.3-2.7 |  |  |  |  | 29.9
| 2.7-4.5 |  |  |  |  | 18.9
| 4.5-6.5 |  |  |  |  | 0.3
| 6.5-9.7 |  |  |  |  | 0.5
| 9.7-15 |  |  |  |  | 1
| >15 |  |  |  |  | 5.8

## feed
Feedstreams
* | 843C1 | Trial Burn |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | NG | NG | NG | NG |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Heavy Oils |  | Heavy Oils |  | Heavy Oils |  | Heavy Oils | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 4554 |  | 4483 |  | 4621 |  | 4552.6667 | 4072 | 4072 | 4067 | 4070.3333 |  | 22.3 |  | 22.3 |  | 22.3 |  | 22.3
| Thermal Feedrate |  | MMBtu/hr |  | 72.2 |  | 71.4 |  | 73.4 |  | 72.3333 | 81.44 | 81.44 | 81.34 | 81.4067 | [9 empty] | 153.64 |  | 152.84 |  | 154.74 |  | 153.74
| Viscosity |  | cps |  | 32 |  | 34 |  | 32 |  | 32.6667
| Heating Value |  | Btu/lb |  | 16000 |  | 16000 |  | 16000 |  | 16000
| Density |  | lb/gal |  | 8.9 |  | 8.9 |  | 8.9 |  | 8.9
| Ash |  | lb/hr |  | 1.4 |  | 1.9 |  | 1.2 |  | 1.5 | [5 empty] | 4.39 |  | 4.39 |  | 4.39 |  | 4.39
| Chlorine |  | lb/hr |  | 0.0792 |  | 0.109 |  | 0.0846 |  | 0.090933
| Antimony |  | g/hr |  | 0.51 |  | 0.4 | nd | 0.2 |  | 0.37
| Arsenic |  | g/hr |  | 0.039 |  | 0.035 |  | 0.029 |  | 0.034333
| Barium |  | g/hr |  | 0.15 |  | 0.12 |  | 0.1 |  | 0.12333
| Beryllium |  | g/hr | nd | 0.03 | nd | 0.03 | nd | 0.03 |  | 0.03
| Cadmium |  | g/hr | nd | 0.2 | nd | 0.2 | nd | 0.2 |  | 0.2
| Chromium |  | g/hr |  | 0.27 |  | 0.26 |  | 0.33 |  | 0.28667
| Lead |  | g/hr | nd | 0.4 | nd | 0.4 | nd | 0.4 |  | 0.4
| Mercury |  | g/hr | nd | 0.04 | nd | 0.04 | nd | 0.04 |  | 0.04
| Nickel |  | g/hr | nd | 1 | nd | 1 | nd | 1 |  | 1
| Selenium |  | g/hr |  | 0.78 |  | 0.5 |  | 1.1 |  | 0.79333
| Silver |  | g/hr | nd | 0.06 |  | 0.2 |  | 0.17 |  | 0.14333
| Thallium |  | g/hr | nd | 0.4 | nd | 0.4 | nd | 0.4 |  | 0.4
| Zinc |  | g/hr |  | 3.8 |  | 3.4 |  | 4.2 |  | 3.8
| Stack Gas Flowrate |  | dscfm |  | 32300 |  | 32900 |  | 32500 |  | 32600 | [5 empty] | 32300 |  | 32900 |  | 32500 |  | 32600
| Oxygen |  | % |  | 5.2 |  | 5.1 |  | 5 |  | 5.1 | [5 empty] | 5.2 |  | 5.1 |  | 5 |  | 5.1
| Estimated Firing Rate |  | MMBtu/hr | [21 empty] | 162.0127 |  | 166.0667 |  | 165.0794 |  | 164.5524
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 10.2687 |  | 13.5959 |  | 8.6382 |  | 10.8343 | [5 empty] | 32.1996 |  | 31.4136 |  | 31.6015 |  | 31.7382 | 0 | 42.4683 | 0 | 45.0095 | 0 | 40.2397 | 0 | 42.5725
| Chlorine |  | ug/dscm |  | 580.9139 |  | 779.9732 |  | 608.9943 |  | 656.6271 | [12 empty] | 0 | 580.9139 | 0 | 779.9732 | 0 | 608.9943 | 0 | 656.6271
| Antimony |  | ug/dscm |  | 8.2395 |  | 6.3046 | 100 | 3.1712 | 17.9007 | 5.9051 | [12 empty] | 0 | 8.2395 | 0 | 6.3046 | 100 | 3.1712 | 17.9007 | 5.9051
| Arsenic |  | ug/dscm |  | 0.63008 |  | 0.55165 |  | 0.45982 |  | 0.54718 | [12 empty] | 0 | 0.63008 | 0 | 0.55165 | 0 | 0.45982 | 0 | 0.54718
| Barium |  | ug/dscm |  | 2.4234 |  | 1.8914 |  | 1.5856 |  | 1.9668 | [12 empty] | 0 | 2.4234 | 0 | 1.8914 | 0 | 1.5856 | 0 | 1.9668
| Beryllium |  | ug/dscm | 100 | 0.48468 | 100 | 0.47284 | 100 | 0.47567 | 100 | 0.47773 | [12 empty] | 100 | 0.24234 | 100 | 0.23642 | 100 | 0.23784 | 100 | 0.47773
| Cadmium |  | ug/dscm | 100 | 3.2312 | 100 | 3.1523 | 100 | 3.1712 | 100 | 3.1849 | [12 empty] | 100 | 1.6156 | 100 | 1.5761 | 100 | 1.5856 | 100 | 3.1849
| Chromium |  | ug/dscm |  | 4.3621 |  | 4.098 |  | 5.2324 |  | 4.5642 | [12 empty] | 0 | 4.3621 | 0 | 4.098 | 0 | 5.2324 | 0 | 4.5642
| Lead |  | ug/dscm | 100 | 6.4624 | 100 | 6.3046 | 100 | 6.3423 | 100 | 6.3698 | [12 empty] | 100 | 3.2312 | 100 | 3.1523 | 100 | 3.1712 | 100 | 6.3698
| Mercury |  | ug/dscm | 100 | 0.64624 | 100 | 0.63046 | 100 | 0.63423 | 100 | 0.63698 | [12 empty] | 100 | 0.32312 | 100 | 0.31523 | 100 | 0.31712 | 100 | 0.63698
| Nickel |  | ug/dscm | 100 | 16.1559 | 100 | 15.7615 | 100 | 15.8558 | 100 | 15.9244 | [12 empty] | 100 | 8.0779 | 100 | 7.8807 | 100 | 7.9279 | 100 | 15.9244
| Selenium |  | ug/dscm |  | 12.6016 |  | 7.8807 |  | 17.4413 |  | 12.6412 | [12 empty] | 0 | 12.6016 | 0 | 7.8807 | 0 | 17.4413 | 0 | 12.6412
| Silver |  | ug/dscm | 100 | 0.96935 |  | 3.1523 |  | 2.6955 | 14.2194 | 2.2724 | [12 empty] | 100 | 0.96935 | 0 | 3.1523 | 0 | 2.6955 | 14.2194 | 2.2724
| Thallium |  | ug/dscm | 100 | 6.4624 | 100 | 6.3046 | 100 | 6.3423 | 100 | 6.3698 | [12 empty] | 100 | 6.4624 | 100 | 6.3046 | 100 | 6.3423 | 100 | 6.3698
| Zinc |  | ug/dscm |  | 61.3924 |  | 53.5891 |  | 66.5942 |  | 60.5252 | [12 empty] | 0 | 61.3924 | 0 | 53.5891 | 0 | 66.5942 | 0 | 60.5252
| SVM |  | ug/dscm | 100 | 9.6935 | 100 | 9.4569 | 100 | 9.5135 | 100 | 9.5546 | [12 empty] | 100 | 9.6935 | 100 | 9.4569 | 100 | 9.5135 | 100 | 9.5546
| LVM |  | ug/dscm | 8.8496 | 5.4768 | 9.2308 | 5.1225 | 7.7121 | 6.1679 | 8.5476 | 5.5891 | [12 empty] | 8.8496 | 5.4768 | 9.2308 | 5.1225 | 7.7121 | 6.1679 | 8.5476 | 5.5891
* | 843C2 | Trial burn |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Heavy Oils |  | Heavy Oils |  | Heavy Oils |  | Heavy Oils | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 2410 |  | 2369 |  | 2369 |  | 2382.6667 | 3538 | 3538 | 3537 | 3537
| Thermal Feedrate |  | MMBtu/hr |  | 38 |  | 38 |  | 38 |  | 38 | 70.76 | 70.76 | 70.74 | 70.74 |  | 108.76 |  | 108.76 |  | 108.74 |  | 108.74
| Viscosity |  | cps |  | 33 |  | 32 |  | 33 |  | 32.7
| Heating Value |  | Btu/lb |  | 16000 |  | 16000 |  | 16000 |  | 16000
| Density |  | lb/gal |  | 8.9 |  | 8.9 |  | 8.9 |  | 8.9
| Ash |  | lb/hr |  | 0.54 |  | 0.51 |  | 0.59 |  | 0.547
| Chlorine |  | lb/hr |  | 0.032 |  | 0.046 |  | 0.035 |  | 0.038
| Acetophenone |  | g/hr | [7 empty] | 190000
| Stack Gas Flowrate |  | dscfm |  | 32400 |  | 32200 |  | 33200 |  | 32600
| Oxygen |  | % |  | 5.2 |  | 5.1 |  | 5 |  | 5.1
| Estimated Firing Rate |  | MMBtu/hr | [13 empty] | 162.5143 |  | 162.5333 |  | 168.6349 |  | 164.5524
| Ash |  | mg/dscm |  | 3.9486 |  | 3.7288 |  | 4.1576 |  | 3.9502 | [5 empty] | 3.9486 |  | 3.7288 |  | 4.1576 |  | 3.9502
| Chlorine |  | ug/dscm |  | 233.9883 |  | 336.3187 |  | 246.6358 |  | 274.4196 | [5 empty] | 233.9883 |  | 336.3187 |  | 246.6358 |  | 274.4196
* | 843C3 | Risk burn |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Heavy Oils |  | Heavy Oils |  | Heavy Oils |  | Heavy Oils | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 3186 |  | 3034 |  | 3040 |  | 3086.6667 | 1092 | 1035 | 983 | 1036.7
| Thermal Feedrate |  | MMBtu/hr |  | 50.4 |  | 47.8 |  | 47.9 |  | 48.7 | 21.84 | 20.7 | 19.66 | 20.734 |  | 72.24 |  | 68.5 |  | 67.56 |  | 69.434
| Viscosity |  | cps |  | 19.8 |  | 21 |  | 18.6 |  | 19.8
| Heating Value |  | Btu/lb |  | 15800 |  | 15800 |  | 15800 |  | 15800
| Density |  | lb/gal |  | 8.92 |  | 8.91 |  | 8.93 |  | 8.92
| Ash |  | lb/hr |  | 0.685 |  | 0.661 |  | 0.629 |  | 0.65833
| Chlorine |  | lb/hr |  | 0.00956 |  | 0.0121 |  | 0.0122 |  | 0.011287
| Antimony |  | g/hr | nd | 0.17 |  | 0.766 |  | 0.807 |  | 0.581
| Arsenic |  | g/hr | nd | 0.0072 | nd | 0.0069 | nd | 0.0069 |  | 0.007
| Barium |  | g/hr |  | 0.0382 |  | 0.026 |  | 0.0338 |  | 0.032667
| Beryllium |  | g/hr | nd | 0.021 | nd | 0.02 | nd | 0.02 |  | 0.020333
| Cadmium |  | g/hr | nd | 0.11 | nd | 0.11 | nd | 0.11 |  | 0.11
| Chromium |  | g/hr |  | 0.259 |  | 0.292 |  | 0.333 |  | 0.29467
| Lead |  | g/hr |  | 0.33 |  | 0.869 |  | 1.1 |  | 0.76633
| Mercury |  | g/hr | nd | 0.029 | nd | 0.028 | nd | 0.028 |  | 0.028333
| Nickel |  | g/hr | nd | 0.69 | nd | 0.66 | nd | 0.66 |  | 0.67
| Selenium |  | g/hr |  | 0.538 | nd | 0.29 | nd | 0.576 |  | 0.468
| Silver |  | g/hr | nd | 0.041 | nd | 0.039 | nd | 0.039 |  | 0.039667
| Thallium |  | g/hr | nd | 0.26 | nd | 0.25 | nd | 0.25 |  | 0.25333
| Zinc |  | g/hr |  | 0.267 |  | 0.328 |  | 0.258 |  | 0.28433
| Stack Gas Flowrate |  | dscfm |  | 17212 |  | 16546 |  | 16149 |  | 16635.6667
| Oxygen |  | % |  | 7 |  | 6.8 |  | 6.4 |  | 6.7333
| Estimated Firing Rate |  | MMBtu/hr | [13 empty] | 76.4978 |  | 74.5883 |  | 74.8493 |  | 75.3446
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 10.6409 |  | 10.5309 |  | 9.9862 |  | 10.386 |  |  |  |  | 0 | 10.6409 | 0 | 10.5309 | 0 | 9.9862 | 0 | 10.386
| Chlorine |  | ug/dscm |  | 148.5062 |  | 192.7748 |  | 193.6902 |  | 178.3237 |  |  |  |  | 0 | 148.5062 | 0 | 192.7748 | 0 | 193.6902 | 0 | 178.3237
| Antimony |  | ug/dscm | 100 | 5.8167 |  | 26.8805 |  | 28.2205 | 9.5485 | 20.3059 |  |  |  |  | 100 | 5.8167 | 0 | 26.8805 | 0 | 28.2205 | 9.5485 | 20.3059
| Arsenic |  | ug/dscm | 100 | 0.24636 | 100 | 0.24214 | 100 | 0.24129 | 100 | 0.24326 |  |  |  |  | 100 | 0.24636 | 100 | 0.24214 | 100 | 0.24129 | 100 | 0.24326
| Barium |  | ug/dscm |  | 1.3071 |  | 0.91239 |  | 1.182 |  | 1.1338 |  |  |  |  | 0 | 1.3071 | 0 | 0.91239 | 0 | 1.182 | 0 | 1.1338
| Beryllium |  | ug/dscm | 100 | 0.71854 | 100 | 0.70184 | 100 | 0.69939 | 100 | 0.70659 |  |  |  |  | 100 | 0.71854 | 100 | 0.70184 | 100 | 0.69939 | 100 | 0.70659
| Cadmium |  | ug/dscm | 100 | 3.7638 | 100 | 3.8601 | 100 | 3.8467 | 100 | 3.8235 |  |  |  |  | 100 | 3.7638 | 100 | 3.8601 | 100 | 3.8467 | 100 | 3.8235
| Chromium |  | ug/dscm |  | 8.862 |  | 10.2469 |  | 11.6449 |  | 10.2513 |  |  |  |  | 0 | 8.862 | 0 | 10.2469 | 0 | 11.6449 | 0 | 10.2513
| Lead |  | ug/dscm |  | 11.2913 |  | 30.495 |  | 38.4667 |  | 26.751 |  |  |  |  | 0 | 11.2913 | 0 | 30.495 | 0 | 38.4667 | 0 | 26.751
| Mercury |  | ug/dscm | 100 | 0.99227 | 100 | 0.98258 | 100 | 0.97915 | 100 | 0.98467 |  |  |  |  | 100 | 0.99227 | 100 | 0.98258 | 100 | 0.97915 | 100 | 0.98467
| Nickel |  | ug/dscm | 100 | 23.6091 | 100 | 23.1608 | 100 | 23.08 | 100 | 23.2833 |  |  |  |  | 100 | 23.6091 | 100 | 23.1608 | 100 | 23.08 | 100 | 23.2833
| Selenium |  | ug/dscm |  | 18.4083 |  | 10.1767 | 100 | 20.1425 |  | 16.2425 |  |  |  |  | 0 | 18.4083 | 0 | 10.1767 | 100 | 20.1425 | 0 | 16.2425
| Silver |  | ug/dscm | 100 | 1.4029 | 100 | 1.3686 | 100 | 1.3638 | 100 | 1.3784 |  |  |  |  | 100 | 1.4029 | 100 | 1.3686 | 100 | 1.3638 | 100 | 1.3784
| Thallium |  | ug/dscm | 100 | 8.8962 | 100 | 8.773 | 100 | 8.7424 | 100 | 8.8039 |  |  |  |  | 100 | 8.8962 | 100 | 8.773 | 100 | 8.7424 | 100 | 8.8039
| Zinc |  | ug/dscm |  | 9.1357 |  | 11.5102 |  | 9.0222 |  | 9.8894 |  |  |  |  | 0 | 9.1357 | 0 | 11.5102 | 0 | 9.0222 | 0 | 9.8894
| SVM |  | ug/dscm | 25 | 15.0551 | 11.236 | 34.3551 | 9.0909 | 42.3133 | 12.5056 | 30.5745 |  |  |  |  | 25 | 15.0551 | 11.236 | 34.3551 | 9.0909 | 42.3133 | 12.5056 | 30.5745
| LVM |  | ug/dscm | 9.8189 | 9.8269 | 8.4352 | 11.1909 | 7.4743 | 12.5856 | 8.48 | 11.2011 |  |  |  |  | 9.8189 | 9.8269 | 8.4352 | 11.1909 | 7.4743 | 12.5856 | 8.48 | 11.2011

## process
Process Information
Cond Avg
843C1 | Trial burn
Comb Temp | oF | 2182
Prod Rate | lb/hr | 129377
Max Comb Air Flow | lb/hr | 213645
843C2 | Trial burn
Comb Temp | oF | 1729
Prod Rate | lb/hr | 90118
Max Comb Air Flow | lb/hr | 210084
843C3 | Risk burn
Comb Temp | oF | 1769.3
Prod Rate | lb/hr | 58647.7
Max Comb Air Flow | lb/hr | 101584

## df c3
PCDD/PCDF
N
Facility Name and ID: |  | Dow Chemical Company, Freeport, TX
Condition ID: |  | 843C3
Condition/Test Date: |  | Risk burn, slightly above normal operating of liq waste feed rate, normal comb temp, February 10-11, 1998.
|  | I-TEF |  | Run 1 |  |  |  |  | Run 2 |  |  |  |  | Run 3
|  | Wght Fact |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ
|  |  |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND
Detected in sample volume (pg)
| 2,3,7,8-TCDD | 1 | nd | 4 | 4 | 2 | 2 | nd | 6.5 | 6.5 | 3.25 | 3.25 | nd | 5.8 | 5.8 | 2.9 | 2.9
| Total TCDD | 0 |  | 23 | 0 | 23 | 0 | nd | 6.9 | 0 | 3.45 | 0 | nd | 5.8 | 0 | 0 | 0
| 1,2,3,7,8-PCDD | 0.5 | nd | 4.6 | 2.3 | 2.3 | 1.15 | nd | 5 | 2.5 | 2.5 | 1.25 | nd | 4.3 | 2.15 | 2.15 | 1.075
| Total PCDD | 0 | nd | 4.6 | 0 | 2.3 | 0 | nd | 5 | 0 | 2.5 | 0 | nd | 4.3 | 0 | 0 | 0
| 1,2,3,4,7,8-HxCDD | 0.1 | nd | 7.9 | 0.79 | 3.95 | 0.395 | nd | 11 | 1.1 | 5.5 | 0.55 | nd | 9.7 | 0.97 | 4.85 | 0.485
| 1,2,3,6,7,8-HxCDD | 0.1 | nd | 6.5 | 0.65 | 3.25 | 0.325 | nd | 8.7 | 0.87 | 4.35 | 0.435 | nd | 8 | 0.8 | 4 | 0.4
| 1,2,3,7,8,9-HxCDD | 0.1 | nd | 6.2 | 0.62 | 3.1 | 0.31 | nd | 8.3 | 0.83 | 4.15 | 0.415 | nd | 7.6 | 0.76 | 3.8 | 0.38
| Total HxCDD | 0 | nd | 7.9 | 0 | 3.95 | 0 | nd | 11 | 0 | 5.5 | 0 | nd | 9.7 | 0 | 4.85 | 0
| 1,2,3,4,6,7,8-HpCDD | 0.01 |  | 14 | 0.14 | 14 | 0.14 | nd | 13 | 0.13 | 6.5 | 0.065 | nd | 14 | 0.14 | 7 | 0.07
| Total HpCDD | 0 |  | 14 | 0 | 14 | 0 | nd | 13 | 0 | 6.5 | 0 | nd | 14 | 0 | 7 | 0
| OCDD | 0.001 |  | 110 | 0.11 | 110 | 0.11 |  | 99 | 0.099 | 99 | 0.099 |  | 100 | 0.1 | 100 | 0.1
| 2,3,7,8-TCDF | 0.1 | nd | 7.4 | 0.74 | 3.7 | 0.37 | nd | 6.7 | 0.67 | 3.35 | 0.335 | nd | 7.6 | 0.76 | 3.8 | 0.38
| Total TCDF | 0 | nd | 7.4 | 0 | 3.7 | 0 | nd | 6.7 | 0 | 3.35 | 0 | nd | 7.6 | 0 | 3.8 | 0
| 1,2,3,7,8-PCDF | 0.05 | nd | 7.2 | 0.36 | 3.6 | 0.18 | nd | 9.1 | 0.455 | 4.55 | 0.2275 | nd | 6 | 0.3 | 3 | 0.15
| 2,3,4,7,8-PCDF | 0.5 | nd | 6.5 | 3.25 | 3.25 | 1.625 | nd | 8.2 | 4.1 | 4.1 | 2.05 | nd | 5.5 | 2.75 | 2.75 | 1.375
| Total PCDF | 0 | nd | 7.2 | 0 | 3.6 | 0 | nd | 9.1 | 0 | 4.55 | 0 | nd | 6 | 0 | 3 | 0
| 1,2,3,4,7,8-HxCDF | 0.1 |  | 8.4 | 0.84 | 8.4 | 0.84 |  | 6.6 | 0.66 | 6.6 | 0.66 | nd | 3.5 | 0.35 | 1.75 | 0.175
| 1,2,3,6,7,8-HxCDF | 0.1 | nd | 3.2 | 0.32 | 1.6 | 0.16 | nd | 4.6 | 0.46 | 2.3 | 0.23 | nd | 3.3 | 0.33 | 1.65 | 0.165
| 1,2,3,7,8,9-HxCDF | 0.1 | nd | 3.2 | 0.32 | 1.6 | 0.16 | nd | 4.6 | 0.46 | 2.3 | 0.23 | nd | 3.3 | 0.33 | 1.65 | 0.165
| 2,3,4,6,7,8-HxCDF | 0.1 | nd | 3.7 | 0.37 | 1.85 | 0.185 | nd | 5.3 | 0.53 | 2.65 | 0.265 | nd | 3.9 | 0.39 | 1.95 | 0.195
| Total HxCDF | 0 |  | 17 | 0 | 17 | 0 |  | 12 | 0 | 12 | 0 | nd | 3.9 | 0 | 1.95 | 0
| 1,2,3,4,6,7,8-HpCDF | 0.01 |  | 52 | 0.52 | 52 | 0.52 |  | 29 | 0.29 | 29 | 0.29 |  | 19 | 0.19 | 19 | 0.19
| 1,2,3,4,7,8,9-HpCDF | 0.01 | nd | 6.9 | 0.069 | 3.45 | 0.0345 | nd | 3.6 | 0.036 | 1.8 | 0.018 | nd | 4.4 | 0.044 | 2.2 | 0.022
| Total HCDF | 0 |  | 52 | 0 | 52 | 0 |  | 29 | 0 | 29 | 0 |  | 19 | 0 | 19 | 0
| OCDF | 0.001 |  | 230 | 0.23 | 230 | 0.23 |  | 110 | 0.11 | 110 | 0.11 |  | 56 | 0.056 | 56 | 0.056
| Gas sample volume (dscf) |  |  |  | 133.884 | 133.884 | 133.884 |  |  | 136.591 | 136.591 | 136.591 |  |  | 131.79 | 131.79 | 131.79
| O2 (%) |  |  |  | 7 | 7 | 7 |  |  | 6.8 | 6.8 | 6.8 |  |  | 6.4 | 6.4 | 6.4
| PCDD/PCDF (pg in sample) |  |  |  | 15.629 | 459.55 | 8.7345 |  |  | 19.8 | 275.85 | 10.4795 |  |  | 16.22 | 195.6 | 8.283
| PCDD/PCDF (ng/dscm @ 7% O2) |  | 88.227 |  | 0.0041249 | 0.12129 | 0.0023053 | 94.1465 |  | 0.0050501 | 0.070356 | 0.0026728 | 97.8668 |  | 0.0041702 | 0.050289 | 0.0021296
| TEQ Cond Avg | 0.0023692
| Total Cond Avg | 0.080645