## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 908
EPA ID No. | WVD005005483
Facility Name | Union Carbide Corporation
Facility Location
City | South Charleston
State | WV
Unit ID Name/No. | Boiler 25
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Coal-fired boiler
Combustor Type | Pulverized, suspension
Combustor Characteristics | Watertube boiler, 323 MMBtu/hr, inlet water at 380F, 6 opposed firing burners
Capacity (MMBtu/hr) | 323
Soot Blowing | Yes, run 3 (8 minutes)
APCS Detailed Acronym | ESP
APCS General Class | ESP
APCS Characteristics | 5 fields
Hazardous Wastes | Liq
Haz Waste Description | Liquid residue wastes
Supplemental Fuel | Coal, natural gas
Pulverized coal
Stack Characteristics
Diameter (ft) | 10
Height (ft) | 150
Gas Velocity (ft/sec) | 25.74
Gas Temperature (°F) | 330.1
Permitting Status | Tier l : Sb, Ba, Hg, Ag, Pb, Tl; Tier lll : As, Be, Cd, Cr, Cl
HWC Burn Status (Date if Terminated)

## cond
Cond Description
908C1
Report Name/Date | Certification of Compliance Boilers #15 and #25, August 1998
Report Prepare | TRC Environmental Corporation
Testing Firm | TRC Environmental Corporation
Testing Dates | 1998-05-18
Cond Dates | 1998-05-01
Condition Descr | CoC, max haz waste feed rate, max load
Content | PM, HCl/Cl2, Cr, Be, Cd, As

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
Sootblow
1 | 908C1 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0517 |  | 0.0224 |  | 0.0228 |  | 0.0365
| CO (MHRA) | E1 | ppmv | y |  | 14 |  | 83 |  | 47 |  | 48
| CO (RA) | E1 | ppmv | y |  | 10 |  | 36 |  | 33 |  | 26.3333
| HCl |  | g/hr |  |  | 28112 |  | 32790 |  | 30830 |  | 30453
| Cl2 |  | g/hr |  |  | 193 |  | 143 |  | 134 |  | 168
| Arsenic |  | g/hr |  |  | 1.3 |  | 1.78 |  | 1.63 |  | 1.54
| Beryllium |  | g/hr |  |  | 0.19 |  | 0.43 |  | 0.42 |  | 0.31
| Cadmium |  | g/hr |  |  | 0.26 |  | 0.26 |  | 0.34 |  | 0.26
| Chromium |  | g/hr |  |  | 3.46 |  | 2.41 |  | 1.52 |  | 2.93
| Chromium (Hex) |  | g/hr |  | nd | 0.02 | nd | 0.021 | nd | 0.02 | nd | 0.02
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 65496 |  | 73547 |  | 73573 |  | 70872
| O2 |  | % |  |  | 7.1 |  | 7.3 |  | 7.2 |  | 7.2
| Moisture |  | % |  |  | 10.5 |  | 10.5 |  | 11 |  | 10.6667
| Temperature |  | °F |  |  | 328.1 |  | 330.9 |  | 325 |  | 328
| Sampling Train | Cr/Cr+6 | E2
| Stack Gas Flowrate |  | dscfm |  |  | 72865 |  | 73232 |  | 76151 |  | 74082.6667
| O2 |  | % |  |  | 7.1 |  | 7.3 |  | 7.2 |  | 7.2
| Moisture |  | % |  |  | 8.4 |  | 8.9 |  | 10.1 |  | 9.1333
| Temperature |  | °F |  |  | 330.9 |  | 332.6 |  | 328.5 |  | 330.6667
| Sampling Train | Metals | E3
| Stack Gas Flowrate |  | dscfm |  |  | 67063 |  | 66951 |  | 72323 |  | 68779
| O2 |  | % |  |  | 7.1 |  | 7.3 |  | 7.2 |  | 7.2
| Moisture |  | % |  |  | 10.6 |  | 10.7 |  | 11.2 |  | 10.8333
| Temperature |  | °F |  |  | 334 |  | 331.7 |  | 329.4 |  | 331.7
| HCl | E1 | ppmv | y |  | 170.0196 |  | 179.1813 |  | 167.1909 |  | 171.4404
| Cl2 | E1 | ppmv | y |  | 0.60023 |  | 0.40183 |  | 0.37368 |  | 0.48635
| Total Chlorine | E1 | ppmv | y |  | 171.22 |  | 179.9849 |  | 167.9383 |  | 172.4131
| Arsenic | E3 | µg/dscm | y |  | 11.7735 |  | 14.5655 |  | 13.2367 |  | 12.9825
| Beryllium | E3 | µg/dscm | y |  | 1.7207 |  | 3.5186 |  | 3.4107 |  | 2.6134
| Cadmium | E3 | µg/dscm | y |  | 2.3547 |  | 2.1275 |  | 2.761 |  | 2.1918
| Chromium | E3 | µg/dscm | y |  | 31.3355 |  | 19.7207 |  | 12.3434 |  | 24.7004
| Chromium (Hex) | E2 | µg/dscm | y | nd | 0.18113 | nd | 0.17184 | nd | 0.16241 | 100 | 0.1686
| SVM | E3 | µg/dscm | y |  | 2.3547 |  | 2.1275 |  | 2.761 |  | 2.1918 | Cd only
| LVM | E3 | µg/dscm | y |  | 44.8297 |  | 37.8048 |  | 28.9909 |  | 40.2962

## feed
Feedstreams
* | 908C1 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3 | F4 | F4 | F4 | F4 | [5 empty] | F5 |  | F5 |  | F5 |  | F5
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike |  | Coal |  | Coal |  | Coal |  | Coal | Spike | Spike | Spike | Spike | [5 empty] | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW | [5 empty] | Coal |  | Coal |  | Coal |  | Coal |  |  |  |  | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Liq waste resid |  | Liq waste resid |  | Liq waste resid |  | Liq waste resid | Waste spike | Waste spike | Waste spike | Waste spike |  | Coal |  | Coal |  | Coal |  | Coal | Coal spike | Coal spike | Coal spike | Coal spike | [5 empty] | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 4503 |  | 4500.6 |  | 4503.6 |  | 4504 | [5 empty] | 18120 |  | 19842 |  | 20010 |  | 19326
| Viscosity | cps |  | 7.1 |  | 5.7 |  | 4 |  | 5.6
| Heating Value | Btu/lb |  | 6300 |  | 5300 |  | 5300 |  | 5633 | [5 empty] | 12975 |  | 12948 |  | 12933 |  | 12952
| Moisture | wt % | [13 empty] | 1.22 |  | 1.2 |  | 1.32 |  | 1.25
| Ash | g/hr | nd | 2043 | nd | 2041 | nd | 2043 |  | 2043 | [5 empty] | 955027 |  | 1048648 |  | 1045599 |  | 1016425
| Chlorine | g/hr |  | 531 |  | 367 |  | 159 |  | 353 | 5722 | 5684 | 5905 | 5770 |  | 8019.9482 |  | 7906.964 |  | 7070.422 |  | 7665.7781 | 14873 | 14873 | 14873 | 14873
| Arsenic | g/hr |  | 1.2 |  | 1 |  | 0.92 |  | 1 | 11 | 11 | 11 | 11 | nd | 8.1187 |  | 17.784 | nd | 8.9562 |  | 11.6196 | 83 | 83 | 83 | 83
| Beryllium | g/hr | nd | 0.051075 | nd | 0.051025 | nd | 0.051075 |  | 0.1 | 15 | 14 | 15 | 15 |  | 11.8536 |  | 11.856 |  | 9.868 |  | 11.1925 | 99 | 99 | 99 | 99
| Cadmium | g/hr | nd | 0.051075 | nd | 0.051025 | nd | 0.051075 |  | 0.1 | 4.8 | 4.8 | 4.9 | 4.8 | nd | 2.4356 | nd | 2.6676 | nd | 2.6869 |  | 2.5967 | 16 | 16 | 16 | 16
| Chromium | g/hr | nd | 0.51075 | nd | 0.5103 | nd | 0.51075 |  | 0.1 | 73 | 72 | 75 | 73 |  | 224.2306 |  | 228.228 |  | 247.6868 |  | 233.3818 | 193 | 193 | 193 | 193
| Antimony | g/hr | nd | 20 | nd | 20 | nd | 20 |  | 20 | [5 empty] | 7.9024 |  | 8.892 |  | 17.7624 |  | 11.5189
| Barium | g/hr | nd | 1 | nd | 1 | nd | 1 |  | 1 | [5 empty] | 681.582 |  | 711.36 |  | 759.836 |  | 717.5927
| Lead | g/hr | nd | 10 | nd | 10 | nd | 10 |  | 10 | [5 empty] | 72.1094 |  | 61.256 |  | 62.1684 |  | 65.1779
| Mercury | g/hr | nd | 0.02 | nd | 0.02 | nd | 0.02 |  | 0.02 | [5 empty] | 0.39512 |  | 0.3952 |  | 0.19736 |  | 0.32923
| Silver | g/hr | nd | 1 | nd | 1 | nd | 1 |  | 1 |  |  |  |  | nd | 1.9756 | nd | 2.964 | nd | 2.9604 |  | 2.6333
| Thallium | g/hr | nd | 2 | nd | 2 | nd | 2 |  | 2 | [5 empty] | 7.9024 | nd | 8.892 | nd | 8.8812 |  | 8.5585
| Stack Gas Flowrate | dscfm |  | 65496 |  | 73547 |  | 73573 |  | 70872 | 65496 | 73547 | 73573 | 70872 |  | 65496 |  | 73547 |  | 73573 |  | 70872 | 65496 | 73547 | 73573 | 70872 | [5 empty] | 65496 |  | 73547 |  | 73573 |  | 70872
| Oxygen | % |  | 7.1 |  | 7.3 |  | 7.2 |  | 7.2 | 7.1 | 7.3 | 7.2 | 7.2 |  | 7.1 |  | 7.3 |  | 7.2 |  | 7.2 | 7.1 | 7.3 | 7.2 | 7.2 | [5 empty] | 7.1 |  | 7.3 |  | 7.2 |  | 7.2
| Thermal Feedrate | MMBtu/hr |  | 28.3689 |  | 23.8532 |  | 23.8691 |  | 25.371 | [5 empty] | 235.107 |  | 256.9142 |  | 258.7893 |  | 250.3104 | [9 empty] | 263.4759 |  | 280.7674 |  | 282.6584 |  | 275.6814
| Estimated Firing Rate | MMBtu/hr | [35 empty] | 310.4869
Feedrate MTEC Calculations
| Ash | mg/dscm | 100 | 18.5024 | 100 | 16.7012 | 100 | 16.5906 | 100 | 17.2647 | [5 empty] | 8649.2096 |  | 8580.9338 |  | 8490.9827 |  | 8573.7087 | [9 empty] | 8667.7121 |  | 8597.635 |  | 8507.5733 |  | 8590.9735
| Chlorine | ug/dscm |  | 4809.0057 |  | 3003.1075 |  | 1291.1893 |  | 3034.4342 | 51821.3384 | 46511.344 | 47952.6597 | 48761.7807 |  | 72632.7245 |  | 64701.5346 |  | 57416.6875 |  | 64916.9822 | 134697.4426 | 121703.5925 | 120778.9852 | 125381.9883 | 186518.781 | 168214.9365 | 168731.6449 | 174143.769 |  | 263960.5112 |  | 235919.5787 |  | 227439.5217 |  | 242439.8706
| Arsenic | ug/dscm |  | 10.8678 |  | 8.1829 |  | 7.471 |  | 8.8406 | 99.6216 | 90.0114 | 89.3276 | 92.9868 | 100 | 73.5273 |  | 145.5239 | 100 | 72.7305 | 50.1258 | 97.2606 | 751.6902 | 679.1769 | 674.0171 | 699.7045 | 851.3117 | 769.1883 | 763.3446 | 792.6913 | 7.8579 | 935.7069 |  | 922.895 | 8.622 | 843.5461 | 5.4126 | 900.716
| Beryllium | ug/dscm | 100 | 0.46256 | 100 | 0.41753 | 100 | 0.41476 | 100 | 0.43162 | 135.8476 | 114.56 | 121.8103 | 124.0726 |  | 107.3522 |  | 97.0159 |  | 80.1349 |  | 94.8344 | 896.5943 | 810.1026 | 803.9481 | 834.5873 | 1032.4419 | 924.6625 | 925.7584 | 958.6599 |  | 1140.2567 |  | 1022.096 |  | 1006.3081 |  | 1056.2203
| Cadmium | ug/dscm | 100 | 0.46256 | 100 | 0.41753 | 100 | 0.41476 | 100 | 0.43162 | 43.4712 | 39.2777 | 39.7914 | 40.8468 | 100 | 22.0582 | 100 | 21.8286 | 100 | 21.8191 | 100 | 21.902 | 144.9041 | 130.9257 | 129.931 | 134.8828 | 188.3754 | 170.2034 | 169.7224 | 175.7296 | 10.6786 | 210.8961 | 11.5595 | 192.4495 | 11.5828 | 191.9563 | 11.2549 | 198.434
| Chromium | ug/dscm | 100 | 4.6256 | 100 | 4.1757 | 100 | 4.1476 | 100 | 4.3163 | 661.1251 | 589.1655 | 609.0516 | 619.7807 |  | 2030.7462 |  | 1867.5565 |  | 2011.3871 |  | 1969.8966 | 1747.906 | 1579.2909 | 1567.2927 | 1627.0237 | 2409.0311 | 2168.4564 | 2176.3442 | 2246.8044 |  | 4444.4029 |  | 4040.1886 |  | 4191.879 |  | 4225.4902
| Antimony | ug/dscm | 100 | 181.1302 | 100 | 163.6571 | 100 | 162.4137 | 100 | 169.067 | [5 empty] | 71.5681 |  | 72.7619 |  | 144.2429 |  | 96.191 | [8 empty] | 71.6784 | 252.6983 | 69.2233 | 236.419 | 52.9627 | 306.6566 | 63.7368 | 265.258
| Barium | ug/dscm | 100 | 9.0565 | 100 | 8.1829 | 100 | 8.1207 | 100 | 8.4533 | [5 empty] | 6172.7528 |  | 5820.9553 |  | 6170.3907 |  | 6054.6996 | [9 empty] | 6181.8093 |  | 5829.1381 |  | 6178.5114 |  | 6063.1529
| Lead | ug/dscm | 100 | 90.5651 | 100 | 81.8285 | 100 | 81.2069 | 100 | 84.5335 | [5 empty] | 653.0594 |  | 501.2489 |  | 504.8501 |  | 553.0528 | [8 empty] | 12.1789 | 743.6244 | 14.0339 | 583.0775 | 13.8565 | 586.057 | 13.2584 | 637.5863
| Mercury | ug/dscm | 100 | 0.18113 | 100 | 0.16366 | 100 | 0.16241 | 100 | 0.16907 | [5 empty] | 3.5784 |  | 3.2339 |  | 1.6027 |  | 2.805 | [8 empty] | 4.8179 | 3.7595 | 4.817 | 3.3975 |  | 1.7651 | 3.8644 | 2.9741
| Silver | ug/dscm | 100 | 9.0565 | 100 | 8.1829 | 100 | 8.1207 | 100 | 8.4533 |  |  |  |  | 100 | 17.892 | 100 | 24.254 | 100 | 24.0405 | 100 | 22.0622 | [8 empty] | 100 | 26.9485 | 100 | 32.4368 | 100 | 32.1612 | 100 | 30.5155
| Thallium | ug/dscm | 100 | 18.113 | 100 | 16.3657 | 100 | 16.2414 | 100 | 16.9067 | [5 empty] | 71.5681 | 100 | 72.7619 | 100 | 72.1214 | 66.9357 | 72.1505 | [8 empty] | 20.1971 | 89.6812 | 100 | 89.1276 | 100 | 88.3628 | 73.2127 | 89.0572
| SVM | ug/dscm | 100 | 91.0276 | 100 | 82.2461 | 100 | 81.6216 | 100 | 84.9651 | 43.4712 | 39.2777 | 39.7914 | 40.8468 | 3.2673 | 675.1176 | 4.1731 | 523.0775 | 4.1429 | 526.6693 | 3.8093 | 574.9548 | 144.9041 | 130.9257 | 129.931 | 135.2536 | 188.3754 | 170.2034 | 169.7224 | 176.1004 | 11.8474 | 954.5206 | 13.4199 | 775.527 | 13.2955 | 778.0133 | 12.7828 | 836.0203
| LVM | ug/dscm | 31.8888 | 15.956 | 35.9518 | 12.7761 | 37.9144 | 12.0334 | 34.9409 | 13.5885 | 896.5943 | 793.7369 | 820.1894 | 836.8402 | 3.3246 | 2211.6258 | 0 | 2110.0963 | 3.3605 | 2164.2525 | 2.255 | 2161.9915 | 3396.1905 | 3068.5704 | 3045.2578 | 3170.0062 | 4292.7848 | 3862.3072 | 3865.4472 | 4006.8464 | 1.1277 | 6520.3665 | 0 | 5985.1796 | 1.2038 | 6041.7332 | 0.78857 | 6182.4264
BIF Feedrate Limits
| Antimony | g/hr | [7 empty] | 1550
| Arsenic | g/hr | [7 empty] | 101
| Barium | g/hr | [7 empty] | 258442
| Beryllium | g/hr | [7 empty] | 126
| Cadmium | g/hr | [7 empty] | 20
| Chromium | g/hr | [7 empty] | 502
| Lead | g/hr | [7 empty] | 465
| Mercury | g/hr | [7 empty] | 413
| Silver | g/hr | [7 empty] | 15506
| Thallium | g/hr | [7 empty] | 2584

## process
Process Information
908C1 |  | Cond Avg
Steam Prod | lb/hr | 262000
Comb Temp | F | 784
ESP Power Input | kVA | 35.2
ESP Inlet Temp | F | 355